## Instructions for specs
Please read the instructions carefully to ensure that all required documentation is submitted.
Only complete bids with all tabs filled and supplemental documentation attached will be considered.
Tab: "1 - VIE Civils Requirements
This table contains the design and construction requirements for the VIE civils included in the RFP.
Please review these requirements carefully before preparing the technical proposal.
Contractors must submit proposals indicating that these requirements are met.
Tab: "2 - Cylinder Storage Requirements"
This table contains the design and construction requirements for the cylinder storage room included in the RFP.
Please review these requirements carefully before preparing the technical proposal.
Contractors must submit proposals indicating that these requirements are met.
Tab: "3 - VIE System & Filling Station Plan"
This table contains the layout design requirements for the VIE System & Filling Station included in the RFP.
Please review these requirements carefully before preparing the technical proposal.
Contractors must submit proposals indicating that these requirements are met.
Tab: "4 - VIE Tank Plinth DWG Plan"
This table contains the Plinth design plan and construction requirements for EACH of the VIE Tanks included in the RFP.
Please review these requirements carefully before preparing the technical proposal.
Contractors must submit proposals indicating that these requirements are met.
Query period: | Before 1pm, 24/06/2022
Query email address: | gemprocurement@clintonhealthaccess.org

## 1. VIE Civils
ANNEX B - SPECIFICATION AND CHECKLISTS VIE CIVILS - MAFETENG HOSP VIE PROJECT
Component | Specification | Meet requirement? | Type of supporting documents | Comments
Overview | Civils shall be performed at the designated sites for VIE installation which is A1 as labeled on the Mafeteng Hospital campus map below.
Activities shall include:
• Excavation
• Construction of slab for VIE system
• Preparation for Tanker Truck Access including Tarmacking of road surface
• Third party inspection by Authorized Inspection Authority (AIA), testing, and commissioning
Technical Requirements | Design and construction of slab shall be carried out per requirements and design DWGs provided by Air Products (see Tab: "3 - VIE System & Filling Station Plan" and Tab: "4 - VIE Tank Plinth Plan")
Slab shall be of reinforced concrete construction
Slab shall bear loading of 2 x 13,000 L vertical bulk storage tanks, ambient vaporizer, and liquid-to-gas filling station including cryopump, high pressure vaporizer, and filling ramp.
Achieve necessary compressive strength according to Air Products DWGs and requirements
Security features installed per requirements provided by [insert LOX supplier name], such as:
• Fencing
• Lockable access gates
• Signage (Restricted access, no parking, safety, no smoking)
Testing and Commissioning | To be verified and validated by design engineers as per system-specific configurations.
On-site: Inspection by authorized inspection authority (AIA), testing and commissioning shall be done before handover.
Provision of:
· Third party inspection report for VIE civils
· Testing report
· Commissioning report & certificate

## 2. Cylinder Storage
MAFETENG VIE PROJECT CIVILS - CYLINDER STORAGE
Component | Specification | Meet requirement? | Type of supporting documents | Comments
Overview | Civils shall be performed at the designated sites for cylinder storage structure [insert schematic indicating designated sites]
Activities shall include:
• Excavation
• Construction of slab
• Construction of cylinder storage room
• Inspection and handover
Technical Requirements | Design and construction of cylinder storage shall be carried out as per:
• HTM-02-01: United Kingdom Department of Health: Health Technical Memorandum 02-01: Medical Gas Pipeline Systems -Part A Design, Installation, Validation and Verification
Or
• NFPA 99: National Fire Protection Association (USA): Health Care Facilities Code Handbook
Dedicated, adequate, and safe space for storage of at least 600 high-pressure oxygen gas cylinders for medical use
Outdoor enclosure constructed of non-combustible or limited-combustible materials
• Space shall have at least one external wall to facilitate natural ventilation
Well ventilated
Ambient temperature shall be maintained within range of 10-40 deg Celsius
Sufficient space shall be provided for maneuvering and handling cylinders
Lighting illumination level: 150 lux by means of bulkhead light fittings
Security and access features shall include:
• Provision of adequte space for vehicular access, easy maneuvering of trolleys, and safe cylinder loading/unloading
• Signage (Outside - restricted access, no parking, safety, no smoking; Inside - full vs. empty)
• At least 2 lockable doors or gates
- Open outwards
- Large enough to facilitate cylinder loading/unloading
• Smoke detectors
Storage room shall configured so that cylinders can be held in place, either by racks or zinc-plated brackets or chains.

## RFI_MFLab (hidden)
| 关于产品 | [9 empty] | 关于贵司
产品类型 Product Type | 产品标准要求 Product Specifications | 产品型号（请列出贵公司符合左侧标准要求的产品，并邮件提供电子版产品用户手册） Product Model (s) | 产品排期（假设下周下订单，预计能够供的最早出货排期至何时（日期）？ Lead time if order placed next week (date) | 本次订单所需数量 Units Required | 公司当前可出售的数量 Units Available | 法规批准/认证Regulatory Approval/Certification |  | 产品性能标准Standards, for product performance |  | 产品单价（美金） Unit price (USD) | 制造商标准 Standards, for manufacturer |  | 预付款要求 Pre-payment requirement | 公司以前有向埃塞俄比亚出口的经验吗？Does company have previous export experience to Ethiopia? | 图片示例 Picture
[6 empty] | 标准 | 如果有，请填写 “X” | 标准 | 如果有，清填写 “X” |  | 标准 | 如果有，清填写 “X”
简单氧气气面罩 Simple Face Masks | 成人式： 医用级 | LB1110, Adult(LA), 5.5mm x 2m绿色管 |  | 2000 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X | 生产前付清 | 有
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
ISO 18190
[8 empty] | ISO18562-1 | X
ISO/DIS 23368
[8 empty] | ISO/DIS 17256 | X
[8 empty] | ISO 15223-1 | X
不重吸面罩 Oxygen Mask with reservoir bag | 成人式： 氧气浓度：支持80%至100％的氧气浓度 管长: 2m 使用标准接头；管路（氧气管线）不弯曲 材质：聚氯乙烯（PVC）； 透明；医用级 | LB1310, Adult(LA), 5.5mm x 2m绿色管 氧袋1000ml |  | 2000 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
ISO 18190
[8 empty] | ISO18562-1 | X
ISO/DIS 23368
[8 empty] | ISO/DIS 17256 | X
[8 empty] | ISO 15223-1 | X
文丘里面罩（氧浓度可调面罩） Venturi Mask | 成人式：能以8至10 L / min 的流速输送低至中等流量的氧气，特定氧浓度为30％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,31%(氧气流速6L/min±10%),白色，其他符合 |  | 300 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
| 成人式：能以10至12 L / min 的流速输送低至中等流量的氧气，特定氧浓度为40％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,40%(氧气流速8L/min±10%),粉色，其他符合 |  | 300 |  | CE | X | ISO 18190
[6 empty] | FDA | X | ISO18562-1 | X
[6 empty] | 出口许可证 | X | ISO/DIS 23368
| 成人式：能以12至15 L / min 的流速输送低至中等流量的氧气，特定氧浓度为60％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,60%(氧气流速8L/min±10%),红色，其他符合 |  | 300 |  | CE | X | ISO/DIS 17256 | X
[6 empty] | FDA | X | ISO 15223-1 | X
[6 empty] | 出口许可证 | X
非侵入性/ CPAP口罩 Non-Invasive/CPAP Masks | 入口细菌过滤器（如果适用）（至少180）。 呼气过滤器，效率高。重复使用，可以承受高级消毒和灭菌。 中等大小 | LB3041,不带细菌过滤器，全硅胶，面罩+支架+头带, M |  | 130 |  | CE |  | ISO 18562-1:2017 | X |  | ISO9001 | X
[6 empty] | FDA |  | ISO 17510:2015 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X |  |  |  | ISO14971 | X
非侵入性/ CPAP口罩 Non-Invasive/CPAP Masks | 入口细菌过滤器（如果适用）（至少180）。 呼气过滤器，效率高。重复使用，可以承受高级消毒和灭菌。 大码。 | LB3041,不带细菌过滤器，全硅胶，面罩+支架+头带，L |  | 130
气管导管 Endotracheal Tube | 管： 尺码：7。 内径：7.0mm。 外径：9.3mm。 长度：最小320mm。 接头： 近端：标准内径：15mm。 远端（适合管子）：长度：最小16mm。 袖口： 直径：24mm | LB5010C, 带囊，ID 7.0mm,其他符合 |  | 350 |  | CE | X | ISO 5361:2016 | X |  | ISO9001 | X
[6 empty] | FDA |  | ISO 10993-1:2018 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO 11135:2014 | X |  | ISO14971 | X
| 管： 尺码：7.5 内径：7.5mm。长度：最小320mm。 接头： 近端：标准内径：15mm。 远端（适合管子）：长度：最小16mm。 | LB5010C, 带囊，ID 7.5mm,其他符合 |  | 350 |  | CE | X | ISO 5361:2016 | X
[6 empty] | FDA |  | ISO 10993-1:2018 | X
[6 empty] | 出口许可证 | X | ISO 11135:2014 | X