## Instructions for specs
Please read the instructions carefully to ensure that all required documentation is submitted.
Only complete bids with all tabs filled and supplemental documentation attached will be considered.
Tab: "1 - MGPS Design Requirements"
This table contains the design requirements for the medical gas pipeline system(s) included in the RFP.
Please review these requirements carefully before preparing the technical proposal.
Vendors must submit proposals indicating that these requirements are met.
Tab: "2 - Submission Checklist"
This table contains a summary of the key documentation that must be submitted for a bid to be considered complete.
Please fill columns C, D, E as you prepare documents for your proposal and fill out the subsequent tabs of this spreadsheet.
For standards, please note that compliance to recent equivalents may be accepted upon review.
Tab: "3a, 3b, 3c - Distribution Manifolds"
This is the target performance parameters for the following types of manifold systems:
3a. Manual Manifold
3b. Semi-automatic manifold
3c. Automatic manifold
Complete the specifications tab for the type of manifold(s) requested in Tab 1 - MGPS Design Requirements
Fill column D to indicate whether the product complies with the specification.
Fill column E to indicate what type of supporting documentation is being provided as evidence of compliance with the specification.
Fill column F with comments as applicable. If "other" is selected in Column E, please specify the type of document.
Tab: "4 - Accessories"
This is the target performance parameters for the following types of manifold systems:
4a. Flowmeters
4b. Humidifiers
Fill column D to indicate whether the product complies with the specification.
Fill column E to indicate what type of supporting documentation is being provided as evidence of compliance with the specification.
Fill column F with comments as applicable. If "other" is selected in Column E, please specify the type of document.
Query period: |  | 13TH JULY 2022 to 2ND AUGUST 2022
Query email address: |  | GhanaUNITAIDOxygenProcurement@clintonhealthaccess.org

## 1. MGPS Design Requirements
Component | Specification
Overview | The pipeline distribution network shall tie in to existing manifold system and shall aim to have the following reach across facility:
Enchi Government Hospital
Pediatric & NICU : 4 Male Ward: 3 Female ward: 3 Maternity and labour ward: 3 Theatre and Recovery: 3 Accident and Emergency:5
System configuration shall include:
· semi-automatic oxygen distribution manifold system
· Line valve assemblies
· Area valve service units
· Alarms
· Emergency inlet port
· Terminal units
Piping shall be concealed in the ceiling voids wherever possible and shall be installed in trunking where it is exposed.
Piped network design | Design, installation, testing, and commissioning of medical gas pipelines should be carried out as per:
• HTM-02-01: United Kingdom Department of Health: Health Technical Memorandum 02-01: Medical Gas Pipeline Systems -Part A Design, Installation, Validation and Verification
Or
• NFPA 99: National Fire Protection Association (USA): Health Care Facilities Code Handbook
Additional terminal units will not affect the existing pipeline network.
Copper pipes | Labeling:
· Colour: International (white) labelled “oxygen”
· The pipe manufacturer’s name and registered trademark shall be marked on each pipe, specification, and either traceable batch number or production date
Cleaning:
· Copper piping shall be free of contaminants such as oil, grease, and other readily oxidizable materials.
Each pipe shall be internally clean in such way to prevent gas contamination and potential explosions.
Pipes shall be sold and delivered capped at both ends to minimize contamination prior to installation.
· Pipes shall be certified for use for medical gases. Copper pipe shall have certification of origin and documentation to support fitness for medical gas application.
· All fittings (elbows, connectors, tees, reducing tee, reducers) shall be made of degreased medical copper or brass.
Fittings shall come sealed in individual packages.
Alarms | Master alarms should be added to provide system-status overview if warranted by size of facility / reticulation system and technical team is present to perform continuous surveillance.
Local alarms should be placed within services where risk to patient is high if supply disruption occurs (e.g., OTs and post-op, NICU, paediatric ward, ICU, the ER and delivery rooms)
Alarm shall have the following features:
· Audible and visual alarms to indicate abnormal conditions such as:
High and low pressure conditions
Bank changeover for manifolds
Cessation of flow
Initiation and operation of secondary or emergency supply (e.g., manifold)
Any other system abnormality not otherwise stated
· Visual alarm shall remain active even after pressing of “mute” button; Audible alarm shall re-sound if abnormal condition is left unresolved.
· Digital display of line pressure for all the gas lines, with factory-calibrated pressure sensors housed in or adjacent to AVSUs.
· All wall outlets/terminal units should be covered under local and/or master alarms.
· Power supply of [ 220V- 240V, 50 Hz] AC.
· Wall mounted.
Line Valve Assemblies | Constructed of nickel- plated brass
Ball-valve type, operated manually by lever that opens and closes by a 90⁰ turn.
Pneumatically tested for 800 kPa (which is twice the working pressure) and factory degreased for medical gas service
Labelled according to service including direction of flow
Capable of being locked in a fully opened or fully closed position
Area valve service units (AVSUs) | Constructed in metal with transparent plastic cover.
Valves themselves shall be constructed of nickel- plated brass and shall be ball-valve types, cleaned and tested for medical oxygen application.
Features analogue pressure gauges to indicate the pressure in line.
Contains at least one area valve (Oxygen).
Wall outlets / Terminal Units | Terminal unit wall connection type: [BS]
Colour: International (white) labelled “oxygen”
Oxygen Distribution Manifold System | See tab 3
Warranty | All components of the medical oxygen pipeline network shall have a 5-year warranty period after commissioning, in-line with system design life.
The supplier must ensure the availability of spare part for at least 8 years
Testing and commissioning | All the copper pipes shall be inspected by the client or their appointed agents before installation
A specific sticker shall be affixed to the pipe showing the flow direction.
After installation, the system – comprising piping and fittings – shall undergo comprehensive testing, a plan for which shall include but not be limited to leak tests, a standing pressure test (24hrs at 480 kPa [20% greater than operating pressure]), as well as testing for system pressure drops or shocks.
To be verified and validated by design engineers as per system-specific configurations.
On-site: Inspection, testing and commissioning shall be done before handover.
Provision of:
· As-built system drawings
· Testing report
· Commissioning report & certificate
Standards | Pipeline network designer and installer shall hold a valid certificate of a Quality Management Systems (ISO 13485, ISO 9001), where scope of current registration defined for piped networks
Pipeline components must comply with the following standards (or equivalent):
· ISO 7396-1: Medical gas pipeline systems
· ISO 9170‑1: Terminal units for medical gas pipeline systems
· BS EN 13348: Copper and coppery alloys. Seamless, round copper tubes for medical gases or vacuum or equivalent
· BS EN 1057: Copper and copper alloys. Seamless, round copper tubes for water and gas in sanitary and heating applications or equivalent (*n.b. this standard is used for dimensioning of piping)
· BS EN 1254-1: Copper and copper alloys - Plumbing fittings - Fittings with ends for capillary soldering or capillary brazing to copper tubes
· BS EN 1254-4: Copper and copper alloys - Plumbing fittings - Fittings combining other end connections with capillary or compression ends
· ISO 10524 Pressure regulators for use with medical gases
· ISO 21969: High-pressure flexible connections for use with medical gas systems .
Documentation | See tab 2. Submission Checklist

## 2. Submission Checklist
Vendor:
Category | Requirement | Meet requirement? | Type of supporting documents | Comments
Design | According to HTM-02-01 or NFPA99
BOQ aligns with DWGs
Claims of all flows to TUs
Claims of maximum pressure loss through system
Experience | At least 3 years experience in desigining and setting medical gas pipeline networks for hospitals/medical facilities in GHANA or low- and middle-income countries. Please attached a detailed relevant work history.
Documentation of personnel training/qualifications, which may include: - CV of lead system design engineer - Certifications of personnel installing the system - Summary of training program supplier requires of technical team involved in design & install
Training | Certifications of personnel and CV of the Lead System Design Engineer
Documentation summarizing the training program that the supplier requires of all engineers involved in medical gas system installation and design
Warranty | All components should have at least 2 years’ warranty period after commissioning
The supplier must ensure the availability of spare parts for at least 5 years
Within the warranty period, the manufacturer will be responsible for the prompt repair of malfunctioning equipment within the system
Testing and commissioning | On-site: Inspection, testing and commission should be done before handover
Regulatory and Standards for pipelines | Certificate of Quality Management System (either ISO 9001 or ISO 13485 with scope clearly defined)
ISO 7396-1: Medical gas pipeline systems — Part 1: Pipeline systems for compressed medical gases and vacuum Note: Statement of compliance to be provided by the company carrying out design and installation
ISO 9170-1: Terminal units for medical gas pipeline systems
BS EN 13348: Copper and coppery alloys. Seamless, round copper tubes for medical gases or vacuum
BS EN 1057: Copper and copper alloys. Seamless, round copper tubes for water and gas in sanitary and heating applications (*n.b. this standard is used for dimensioning of piping)
EN 1254-1: Copper and copper alloys - Plumbing fittings - Fittings with ends for capillary soldering or capillary brazing to copper tubes
EN 1254-4: Copper and copper alloys - Plumbing fittings - Fittings combining other end connections with capillary or compression ends
Regulatory and Standards for medical devices | Certified Quality Management Systems (ISO 13485)
Regulatory approval under SRA (CE under MDR or US FDA) for all medical devices included in the BOQ such as manifolds, terminal units, flowmeters, and humidifiers
ISO 10524‑2: Pressure regulators for use with medical grade gases (for manifolds)
ISO 21969: High-pressure flexible connections for use with medical gas systems (for manifolds)

## Medical Device Specs
REMINDER: Medical Device Specifications
The specifications listed to the right of this tab are for products that are regulated as medical devices. Thus, proof of SRA (e.g, CE or FDA) and ISO 13485 must be provided for each item.

## 3. Semi-Automatic Manifold
Vendor
Model
Product | Category | Target Product Profile | Meet requirement? | Type of supporting documents | Comments
Semi-Automatic Oxygen Distribution Manifold | Description | The semi-automatic manifold control system shall comply to ISO 7396-1 – medical graded gas pipeline systems, and NHS Health Technical Memorandum HTM 02-01. The manifold shall be supplied fully assembled and factory tested. | N/A | N/A
| Configuration | Configuration: The manifold system includes the following components to operate 2x 10 cylinders (left and right bank):
• High-pressure bank headers, each with:
a high-pressure regulator, sensor and gauge (pressure displayed in both unit bar and psi)
primary pressure relief valve
a wall mounting bracket
• Automatic bank changeover
• Automatic changeover panel, complete with:
Alarm (audible and visual)
Status monitoring
• Cylinder connections
Flexible tailpipe with brass adaptors suitable for connection to bullnose (5/8 inch BSP (F) / BS 341)
Safety check/non-return valves
• Secondary relief valve assembly comprising line pressure release valve and exhaust line
• Supply line isolation valve (lockable)
• Test point (medical gas terminal unit)
• Manifold shall be configured so that cylinders can be held in place, either by brackets or chains (zinc plated).
| Electrical | All electrical components shall be in a separate enclosure to limit dust, water penetration, and simplify electrical connection with alarms.
PCBs shall be linked with plug and socket connectors for easy removal. For added safety the voltage inside the panel shall not exceed 24V D.C.
Power failure shall not disrupt the flow of supply.
| Operational Features | Semi-automatic manifold control shall include the following operational features: | N/A | N/A
• Adjustable manual and automatic working system
• Pressure indication in both headers and line, displayed in analogue on the gauge.
• Adjustable high- and low-pressure alarm status
• Alarms to be duplicated on a display and embedded panel with LEDs.
• Alarm signal to inform user to perform regular preventive maintenance.
• ‘Service Mode’ to manually override (deactivate) alarms during commissioning and service, as well as allowing manual operation selection of a duty bank.
| Testing | The manifold should be suitable to withstand a nominal pressure of 230 bar.
Two stage regulators allow pressure drop lower than 10% on a flow up to 1,750 l/min at 4 bar
The manifold should be tested (hydraulically) to 400 bar pressure and to be supplied along with necessary test certificate.
| Regulation and standards | Bears CE marking under MDR
|  | Conforms with the most current of the following (or equivalent): | N/A | N/A
• HTM-02-01
• ISO 7396-1
|  | Compliance with: | N/A | N/A
• ISO 13485: Medical devices quality management systems
• ISO 1524‑2: Pressure regulators for use with medical grade gases

## 4a. Dual Flowmeters
Vendor
Model
Product | Spec category | Specs, WHO-UNICEF | Meet requirement? | Type of supporting documents | Comments
Dual Flowmeter, Thorpe tube, pressure compensated | Description | A device intended to measure and regulate the flow of a medical gas [e.g. oxygen (O2), carbon dioxide (CO2), nitrous oxide (N2O), helium/oxygen gas mixture (heliox), medical air] during various procedures (e.g. therapeutic administration, anaesthesia, insufflation during surgery). It consists of an upright tube containing a float, which rises and falls in relation to gas flow, and a distal valve (compensated flowmeter) to control gas flow rate. It will be calibrated to a specific medical gas and have a dedicated flow rate range, therefore some types may be dedicated to a specific patient group (e.g. neonate, infant, adult) or clinical use. (SOURCE: GMDN) Oxygen respiration flowmeters are intended for use with a variety of oxygen-supply systems such as central piped systems, cylinders valves, or concentrators and are connected to various delivery modalities or interfaces such as to a patient circuit or a medical device that uses or delivers the gas, including nasal cannulae or various types of mask-patient interfaces. | N/A | N/A
| Technical | Device suitable for use with medical oxygen
Thorpe tube flowmeter type, contains inlet and outlet port, a flow regulator, a valve and a clear measuring tube
dual Type
Flowmeters to measure and regulate flow from an already pressure-reduced and regulated oxygen source to the patient or other medical device
Pressure compensated flowmeters, calibrated at 345–380 kPa (3.4–3.8 bar, 50–55 psi) inlet gauge pressure.
Max gauge inlet pressure 690 kPa (6.9 bar, 100 psi).
Flow adjustment knobs to have rough surface to prevent slipping.
Flowmaters calibrated to the following flow range, all metric (specify):
0-3.5 L/min, accuracy 10%, dual taper graduations 0.25 L/min (0–1 L/min range) and 0.5 L/min (1 L/min – maximum range), or single taper graduations 0.25 L/min full range
0-15 L/min, accuracy 10%, dual taper graduations 0.5 L/min (0–5 L/min range) and 1 L/min (5 L/min – maximum range)
All minimum flowrates to be zero when fully closed
All graduations to be clearly visible for 270 degrees (most breadth for provider vantage points)
Inlet and outlet ports to be clearly specified and will in part be determined by use case (suitable for connection to centralized system):
Piped source inlet: Connection to a terminal unit / bedside unit (e.g. from a piped oxygen network)
BS (3/8 inch BSP female, "British Standard")
Outlets: Specify outlet adapter, e.g., "Christmas tree" barbed tubing adapter, DISS (9/16 inch-18) female to barbed 1/4 inch ID (M) hose connector, DISS humidifier adapter
|  | Flowmeter material: | N/A | N/A
Column to be transparent, clear, shatter-reistant, medical-grade polymer (polypropylene, polycarbonate)
Hardware/valves: Brass/steel/aluminium
All materials in contact with oxygen certified for medical use.
Internal parts (e.g. valve, inlet filter if present), replaceable by user.
|  | Environmental | N/A | N/A
Capable of being stored in ambient temperature of at least 5–50 °C, relative humidity of at least 15–95% non condensing.
Suitable for continuous operation in ambient temperature of at least 5–45 °C, relative humidity of at least 15–90% non condensing.
Specific requirements for altitude may be required, depending on the installation site.
Disinfectable with hospital grade detergents.
| Warranty | 5 years (min. 2)
| QMS | ISO 13485 (medical device QMS)
ISO 14971 (application of risk management)
| Regulatory | CE
FDA
| Product performance standards | ISO 32 Gas cylinders for medical use — Marking for identification of content (or ANSI equivalent)
ISO 5359 Low-pressure hose assemblies for use with medical gases.
ISO 15001 Anaesthetic and respiratory equipment – Compatibility with oxygen.
ISO 15002 Flow-metering devices for connection to terminal units of medical gas pipeline systems.
ISO 15223-1 Medical devices – Symbols to be used with medical device labels, labelling and information to be supplied – Part 1: General requirements.
ISO 18082 Anaesthetic and respiratory equipment – Dimensions of non-interchangeable screw-threaded (NIST) low-pressure connectors for medical gases.
ISO 18562 Biocompatibility evaluation of breathing gas pathways in healthcare applications.
| Packaging | Name and/or trade mark and address of the manufacturer.
Product name.
Product reference.
Type of product and main characteristics.
Performance testing information against the mentioned standards.
Lot number prefixed by the word "LOT" (or equivalent harmonised symbol).
Information for particular storage conditions (temperature, pressure, light, humidity, etc.), as appropriate (or equivalent harmonised symbol), if applicable.
Information for handling, if applicable (or equivalent harmonised symbol).
If the packaging is not transparent, it must bear a diagram (preferably actual size) showing the essential parts of the product and indicating the position of the product in the packaging.
Gross Weight.
Cubic Measurement.
All indicated at least in English.

## 4b. Humidifiers
Vendor
Model
Product | Spec category | Specs, WHO-UNICEF | Meet requirement? | Type of supporting documents | Comments
Humidifier | Description | A device designed to prevent the drying of airway passages associated with the inhalation of oxygen (O2) by adding water vapour to the dry gas as it is passed through, or more seldom, over water. It typically consists of a graduated container (reservoir) for the water, a top piece that functions as a detachable lid (typically a screw lid with a gastight seal), and a tube that protrudes into the water to divert the gas below the water level. This device, commonly known as a bubble humidifier, does not heat the water. It has connectors: 1) one (e.g. a winged nut) that connects to an oxygen therapy flowmeter; and 2) one to which the patient tubing is connected. This is a reusable device. (SOURCE: GMDN 35113) | N/A | N/A
| Technical | Reusable humidifier for oxygen therapy and ventilation/anaesthesia inspiratory lines.
Non-heated humidifier - ambient temperature functionality.
Bubble-through humidification system.
Unbreakable or shatter resistant.
Transparent humidification bottle
Graduated, graduation shall show minimum and maximum water level.
Humidification chamber working volume at least 150 mL, not greater than 500 mL.
Detachable metal or rigid durable polymer cap with gas connectors.
Pressure relief safety valve, ≥ 14 kPa (0.1 bar, 2 psi) pressure rating.
DISS connectors for inlet.
6 mm barbed connector for outlet.
Flow rate capacity up to 15 L/min.
Must be capable of disinfection.
Materials, all to be certified for medical use:
·Cap and connectors made of brass/steel/other biocompatible metal or polymer
·Bottle and tubes made of polypropylene, polycarbonate or equivalent biocompatible plastic/polymer
·Pressure valve made of brass chromium plated or equivalent metal
Supplier must define decontamination procedure.
| Warranty | Min. 1 year (ideal 2)
| Standards | ISO 13485 (medical device QMS)
| Regulatory | CE
FDA
| Product performance standards | ISO 15001 Anaesthetic and respiratory equipment – Compatibility with oxygen.
ISO 15223-1 Medical devices – Symbols to be used with medical device labels, labelling and information to be supplied – Part 1: General requirements.
ISO 18562 Biocompatibility evaluation of breathing gas pathways in healthcare applications.
ISO 18562-1 Biocompatibility evaluation of breathing gas pathways in healthcare applications – Part 1: Evaluation and testing within a risk management process.
| Packaging | Name and/or trade mark and address of the manufacturer.
Product name.
Product reference.
Type of product and main characteristics.
Performance testing information against the mentioned standards.
Lot number prefixed by the word "LOT" (or equivalent harmonised symbol).
Expiry date by year and month, prefixed by the word "EXP" (or equivalent harmonised symbol).
Information for particular storage conditions (temperature, pressure, light, humidity, etc.), as appropriate (or equivalent harmonised symbol), if applicable.
Information for handling, if applicable (or equivalent harmonised symbol).
If the packaging is not transparent, it must bear a diagram (preferably actual size) showing the essential parts of the product and indicating the position of the product in the packaging.
Gross Weight.
Cubic Measurement.
All indicated at least in English.

## RFI_MFLab (hidden)
| 关于产品 | [9 empty] | 关于贵司
产品类型 Product Type | 产品标准要求 Product Specifications | 产品型号（请列出贵公司符合左侧标准要求的产品，并邮件提供电子版产品用户手册） Product Model (s) | 产品排期（假设下周下订单，预计能够供的最早出货排期至何时（日期）？ Lead time if order placed next week (date) | 本次订单所需数量 Units Required | 公司当前可出售的数量 Units Available | 法规批准/认证Regulatory Approval/Certification |  | 产品性能标准Standards, for product performance |  | 产品单价（美金） Unit price (USD) | 制造商标准 Standards, for manufacturer |  | 预付款要求 Pre-payment requirement | 公司以前有向埃塞俄比亚出口的经验吗？Does company have previous export experience to Ethiopia? | 图片示例 Picture
[6 empty] | 标准 | 如果有，请填写 “X” | 标准 | 如果有，清填写 “X” |  | 标准 | 如果有，清填写 “X”
简单氧气气面罩 Simple Face Masks | 成人式： 医用级 | LB1110, Adult(LA), 5.5mm x 2m绿色管 |  | 2000 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X | 生产前付清 | 有
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
ISO 18190
[8 empty] | ISO18562-1 | X
ISO/DIS 23368
[8 empty] | ISO/DIS 17256 | X
[8 empty] | ISO 15223-1 | X
不重吸面罩 Oxygen Mask with reservoir bag | 成人式： 氧气浓度：支持80%至100％的氧气浓度 管长: 2m 使用标准接头；管路（氧气管线）不弯曲 材质：聚氯乙烯（PVC）； 透明；医用级 | LB1310, Adult(LA), 5.5mm x 2m绿色管 氧袋1000ml |  | 2000 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
ISO 18190
[8 empty] | ISO18562-1 | X
ISO/DIS 23368
[8 empty] | ISO/DIS 17256 | X
[8 empty] | ISO 15223-1 | X
文丘里面罩（氧浓度可调面罩） Venturi Mask | 成人式：能以8至10 L / min 的流速输送低至中等流量的氧气，特定氧浓度为30％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,31%(氧气流速6L/min±10%),白色，其他符合 |  | 300 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
| 成人式：能以10至12 L / min 的流速输送低至中等流量的氧气，特定氧浓度为40％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,40%(氧气流速8L/min±10%),粉色，其他符合 |  | 300 |  | CE | X | ISO 18190
[6 empty] | FDA | X | ISO18562-1 | X
[6 empty] | 出口许可证 | X | ISO/DIS 23368
| 成人式：能以12至15 L / min 的流速输送低至中等流量的氧气，特定氧浓度为60％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,60%(氧气流速8L/min±10%),红色，其他符合 |  | 300 |  | CE | X | ISO/DIS 17256 | X
[6 empty] | FDA | X | ISO 15223-1 | X
[6 empty] | 出口许可证 | X
非侵入性/ CPAP口罩 Non-Invasive/CPAP Masks | 入口细菌过滤器（如果适用）（至少180）。 呼气过滤器，效率高。重复使用，可以承受高级消毒和灭菌。 中等大小 | LB3041,不带细菌过滤器，全硅胶，面罩+支架+头带, M |  | 130 |  | CE |  | ISO 18562-1:2017 | X |  | ISO9001 | X
[6 empty] | FDA |  | ISO 17510:2015 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X |  |  |  | ISO14971 | X
非侵入性/ CPAP口罩 Non-Invasive/CPAP Masks | 入口细菌过滤器（如果适用）（至少180）。 呼气过滤器，效率高。重复使用，可以承受高级消毒和灭菌。 大码。 | LB3041,不带细菌过滤器，全硅胶，面罩+支架+头带，L |  | 130
气管导管 Endotracheal Tube | 管： 尺码：7。 内径：7.0mm。 外径：9.3mm。 长度：最小320mm。 接头： 近端：标准内径：15mm。 远端（适合管子）：长度：最小16mm。 袖口： 直径：24mm | LB5010C, 带囊，ID 7.0mm,其他符合 |  | 350 |  | CE | X | ISO 5361:2016 | X |  | ISO9001 | X
[6 empty] | FDA |  | ISO 10993-1:2018 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO 11135:2014 | X |  | ISO14971 | X
| 管： 尺码：7.5 内径：7.5mm。长度：最小320mm。 接头： 近端：标准内径：15mm。 远端（适合管子）：长度：最小16mm。 | LB5010C, 带囊，ID 7.5mm,其他符合 |  | 350 |  | CE | X | ISO 5361:2016 | X
[6 empty] | FDA |  | ISO 10993-1:2018 | X
[6 empty] | 出口许可证 | X | ISO 11135:2014 | X