## Instructions for specs
Please read the instructions carefully to ensure that all required documentation is submitted.
Only complete bids with all tabs filled and supplemental documentation attached will be considered.
Tab: "Tanks (General)"
This table contains general specifications for the bulk storage tanks included in the EOI.
Fill column C to indicate whether the product complies with the specification.
Fill column D to indicate what type of supporting documentation is being provided as evidence of compliance with the specification.
Fill column E with comments as applicable. If "other" is selected in Column E, please specify the type of document.
Tab: "Tanks (Product Specific)"
This table product contains specifications for bulk storage tank product line submitted by vendor in EOI.
Vendors must fill rows 3-8 for product line included in proposal
Tab: "Vaporizers (General)"
This table contains general specifications for ambient/passive vaporizers included in the EOI.
Fill column C to indicate whether the product complies with the specification.
Fill column D to indicate what type of supporting documentation is being provided as evidence of compliance with the specification.
Fill column E with comments as applicable. If "other" is selected in Column E, please specify the type of document.
Tab: "Vaporizers (Product Specific)"
This table product contains specifications for ambient/passive vaporizer product line submitted by vendor in EOI.
Vendors must fill rows 3-7 for product line included in proposal.
Query period: | [insert dates]
Query email address: | gemprocurement@clintonhealthaccess.org

## Tanks (General)
Component | Specification | Meet requirement? | Type of supporting documents | Comments
Design Parameters | Vertical construction, stationary tank type
• Stainless steel or carbon steel outer shell
□ Affixed lifting lugs for use w/ clevis pins
• Stainless steel inner vessel (no aluminum)
• Stainless steel piping
• Vacuum pressure 0.05 bar (or better)
Maximum design pressure / test pressure (MAWP): 18 bar
Minimum / maximum operating temperatures:
• Inner vessel: -196°C /+20°C
• Outer shell: -30 °C /+50 °C
Sizing | See Tab "Tanks (Product Specific)"
Features | Operating:
• Fill coupling / type for LOX (spec type available)
□ Bottom and top-fill lines
• Pressure regulation
□ Pressure build-up/blow-down assembly
□ Pressure regulator with set-point feature for MAOP
• Overfill protection system, comprising
□ Fill line drain valve
□ Trycock vent valve
Monitoring:
• Liquid level gauge (& type to be specified)
• Liquid level transmitter (& type to be specified)
Safety:
•Thermal relief valve
• Safety valves: primary (set at MAOP) and secondary (set at MAWP) (no bursting discs)
Additional offtake:
• Economizer circuit (preferred option)
• Discharge line for liquid offtake (indicate tanks that this is standard on, and if possible, for smaller units)
Documentation | Evidence of effectively managed after sales service, including but not limited to installation, testing, and commissioning, repair, warranties honored, and provision of spare parts
P&ID - generic
Sample databook, illustrative of what would be included (not limited to):
• Manufacturer's declaration of conformity
• 3rd party (e.g., Notified Body for PED) certificate of conformity and test reports, certificates for safety valves
• Commissioning, operations, and maintenance manual
• Detailed stress / loading calculations
Warranty | 2 years minimum
The supplier must ensure the availability of spare parts for the duration of the warranty and indicate lead times
Regulatory | PED 2014/68 EU (indicate NB) Or ASME “U” stamp
QMS | ISO 9001: Quality Management Systems - Requirements
General design guidance (or equivalent) | EN 13458-1: Cryogenic vessels - Static vacuum insulated vessels - Part 1: Fundamental requirements
Process or component specific standards (or equivalent) | EIGA 200/17: The Safe Design, Manufacture, Installation, Operation and Maintenance of Valves Used in Liquid Oxygen and Cold Gaseous Oxygen Systems
ISO 8501-1: Preparation of steel substrates before application of pains and related products – visual assessment of surface cleanliness – Part 1: Rust grades and preparation grades of uncoated steel substrates and of steel substrates after overall removal of previous coatings
ISO 8504-2: Preparation of steel substrates before application of paints and related products – surface preparation methods – part 2: abrasive blast-cleaning
ISO 12944-4: Paints and varnishes – corrosion protection of steel structures by protective paint systems – Part 4: Types of surface and surface preparation
ISO 12944-5: Paints and varnishes – corrosion protection of steel structures by protective paint systems – Part 5: Protective paint systems
ISO 21009-1: Cryogenic vessels – static vacuum-insulated vessels – Part 1: Design, fabrication, inspection, and tests
ISO 21009-2: Cryogenic vessels – Static vacuum insulated vessels – Part 2: Operational requirements
ISO 21010: Cryogenic vessels – Gas/material compatibility
ISO 21013-1: Cryogenic vessels – Gas/material compatibility: Cryogenic vessels – pressure-relief accessories for cryogenic service – Part 1: reclosable pressure relief valves
ISO 23028: Cryogenic vessels – cleanliness for service (specify for LOX service)

## Tanks (Product Specific)
Product availability & associated specifications
Size, Tonnes LOX capacity | 18-20
Equivalent size available, litres
Boil-off rate (indicate conditions)
Discharge capacity (Nm3/hr)
Thermal conductivity
Insulation/fill material
Structural testing: wind & snow loading, earthquake rating

## Vaporizers (General)
Component | Specification | Meet requirement? | Type of supporting documents | Comments
Design Parameters | Ambient/passive vaporizer
• All aluminum
• Rated working pressure: ≥ 36 bar
• Design /maximum allowable working temp -196°C /+50°C
Inlet and outlet flange availability: ASME B16.5, BS PR C1, EN 1092, M40x2 thread, DIN 2635
All models designed according to PED 2014/68/EU, ASME SEC.VIII DIV.I, or ANSI B31.3
Sizing | See Tab "Vaporizers (Product Specific)"
Documentation | Evidence of effectively managed after sales service, including but not limited to installation, testing, and commissioning, repair, warranties honored, and provision of spare parts
Warranty | 1 year minimum
The supplier must ensure the availability of spare parts for the duration of the warranty and indicate lead times
Regulatory | PED 2014/68 EU (indicate NB) Or ASME “U” stamp
QMS | ISO 9001: Quality Management Systems - Requirements

## Vaporizers (Product Specific)
Product availability & associated specifications
Nominal capacity (m3/hr) | 50 | 100
Equivalent size (m3/hr)
Unit weight (dry)
Fin # / fin dimension
Structural testing: wind & snow loading, earthquake rating

## RFI_MFLab (hidden)
| 关于产品 | [9 empty] | 关于贵司
产品类型 Product Type | 产品标准要求 Product Specifications | 产品型号（请列出贵公司符合左侧标准要求的产品，并邮件提供电子版产品用户手册） Product Model (s) | 产品排期（假设下周下订单，预计能够供的最早出货排期至何时（日期）？ Lead time if order placed next week (date) | 本次订单所需数量 Units Required | 公司当前可出售的数量 Units Available | 法规批准/认证Regulatory Approval/Certification |  | 产品性能标准Standards, for product performance |  | 产品单价（美金） Unit price (USD) | 制造商标准 Standards, for manufacturer |  | 预付款要求 Pre-payment requirement | 公司以前有向埃塞俄比亚出口的经验吗？Does company have previous export experience to Ethiopia? | 图片示例 Picture
[6 empty] | 标准 | 如果有，请填写 “X” | 标准 | 如果有，清填写 “X” |  | 标准 | 如果有，清填写 “X”
简单氧气气面罩 Simple Face Masks | 成人式： 医用级 | LB1110, Adult(LA), 5.5mm x 2m绿色管 |  | 2000 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X | 生产前付清 | 有
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
ISO 18190
[8 empty] | ISO18562-1 | X
ISO/DIS 23368
[8 empty] | ISO/DIS 17256 | X
[8 empty] | ISO 15223-1 | X
不重吸面罩 Oxygen Mask with reservoir bag | 成人式： 氧气浓度：支持80%至100％的氧气浓度 管长: 2m 使用标准接头；管路（氧气管线）不弯曲 材质：聚氯乙烯（PVC）； 透明；医用级 | LB1310, Adult(LA), 5.5mm x 2m绿色管 氧袋1000ml |  | 2000 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
ISO 18190
[8 empty] | ISO18562-1 | X
ISO/DIS 23368
[8 empty] | ISO/DIS 17256 | X
[8 empty] | ISO 15223-1 | X
文丘里面罩（氧浓度可调面罩） Venturi Mask | 成人式：能以8至10 L / min 的流速输送低至中等流量的氧气，特定氧浓度为30％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,31%(氧气流速6L/min±10%),白色，其他符合 |  | 300 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
| 成人式：能以10至12 L / min 的流速输送低至中等流量的氧气，特定氧浓度为40％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,40%(氧气流速8L/min±10%),粉色，其他符合 |  | 300 |  | CE | X | ISO 18190
[6 empty] | FDA | X | ISO18562-1 | X
[6 empty] | 出口许可证 | X | ISO/DIS 23368
| 成人式：能以12至15 L / min 的流速输送低至中等流量的氧气，特定氧浓度为60％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,60%(氧气流速8L/min±10%),红色，其他符合 |  | 300 |  | CE | X | ISO/DIS 17256 | X
[6 empty] | FDA | X | ISO 15223-1 | X
[6 empty] | 出口许可证 | X
非侵入性/ CPAP口罩 Non-Invasive/CPAP Masks | 入口细菌过滤器（如果适用）（至少180）。 呼气过滤器，效率高。重复使用，可以承受高级消毒和灭菌。 中等大小 | LB3041,不带细菌过滤器，全硅胶，面罩+支架+头带, M |  | 130 |  | CE |  | ISO 18562-1:2017 | X |  | ISO9001 | X
[6 empty] | FDA |  | ISO 17510:2015 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X |  |  |  | ISO14971 | X
非侵入性/ CPAP口罩 Non-Invasive/CPAP Masks | 入口细菌过滤器（如果适用）（至少180）。 呼气过滤器，效率高。重复使用，可以承受高级消毒和灭菌。 大码。 | LB3041,不带细菌过滤器，全硅胶，面罩+支架+头带，L |  | 130
气管导管 Endotracheal Tube | 管： 尺码：7。 内径：7.0mm。 外径：9.3mm。 长度：最小320mm。 接头： 近端：标准内径：15mm。 远端（适合管子）：长度：最小16mm。 袖口： 直径：24mm | LB5010C, 带囊，ID 7.0mm,其他符合 |  | 350 |  | CE | X | ISO 5361:2016 | X |  | ISO9001 | X
[6 empty] | FDA |  | ISO 10993-1:2018 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO 11135:2014 | X |  | ISO14971 | X
| 管： 尺码：7.5 内径：7.5mm。长度：最小320mm。 接头： 近端：标准内径：15mm。 远端（适合管子）：长度：最小16mm。 | LB5010C, 带囊，ID 7.5mm,其他符合 |  | 350 |  | CE | X | ISO 5361:2016 | X
[6 empty] | FDA |  | ISO 10993-1:2018 | X
[6 empty] | 出口许可证 | X | ISO 11135:2014 | X