## Trolley Specification
Vendor:
Model:
Product | Spec category | Specifications - developed in collaboration with Prabhat (CHAI Cambodia) | Meets requirement? (Yes/No/NA) | Type of supporting document (select from drop down) | Page No. | Comments
Power generator | Generator size: | Capacity: 50 kW
| Engine | Cummins or Perkins type (or equivalent), subject to the engineer’s / consultant’s approval.
· Electronic governor with ISO 8528
· Heavy duty diesel engine
· Cooling system: water and air cooled
· Lubricating oil with fuel filter cartridge
· Heat exchanger for the lubricating oil
· Lubrication is forced by gear pump
· Silenced exhaust muffler (residential type)
· Engine speed 1500 rpm
· Injection type: Direct injection
· Aspiration: turbocharged
· Exhaust manifold
· Flex dilator
· Pump injector with regulator
| Alternator | Stamford, Leroy Somer, ABB, or Marathon type (or equivalent) and subject to the engineer’s / consultant’s approval.
· 3-phase, synchronous, brushless, self-excited
· Self-regulated with Automatic Voltage Regulator (AVR)
· Nominal Power: See generator size
· Nominal Tension: 400/230 V, 3-phase
· RPM: 1500 RPM
· Frequency: 50 Hz
· Protection class: IP 23
· Insulation Class : H
| Control panel | Mounted on the generator for automatic key start on mains having the following instrumentation and protection features:
· Engine temperature gauge
· Battery condition voltmeter
· AC output voltmeter, ammeter, frequency meter for each phase
· Engine start/stop selector switch
· Oil pressure and water temperature gauge
· Over speed and under speed of the engine
· Voltage of alternator out of limit
· Lock up on diesel engine failure to start
· Engine running time meter
· Emergency stop button
· Over current of the alternator detected
· Short circuit in the lines detected
· Three phase and single phase output sockets
· Indicator light and shut down for high engine temp.
· Indicator light and shut down for over speed of the engine
· Indicator light and shut down for belt failure
· Indicator light and shut down for low fuel failure
All the protection and alarms are shown on panel display and as well as meter base set.
Mounted on steel base frame via anti-vibration mount.
| Automatic Transfer Switch (ATS) | According to manufacturer of generator set, match to starting system including necessary accessories.
| Assembly and mounting | The generation sets are fully mounted on electrically welded steel base frames.
| Coupling | The generation sets are coupled by means of plate type coupling which can take any type of vibration initiated from misalignments.
| Fuel tank | · Mounted on a bed frame and it is complete with fuel filter and drain plug connected to the engine with its capacity.
· Capacity as per the load.
· Equipped with flexible return and supply hoses from/to the engine.
| Vibration damper | Vibration damper is incorporated in between the bed plate and the generating set.
| Batteries | Heavy duty lead acid storage batteries, capacity according to manufacturer of generator set. Match battery voltage to starting system, and include necessary cables and clamps’
| Battery Charger | Stand alone / wall mountable, 10A, 240V.
| Mobility/Installation ready | Housing
Compactly designed with the necessary openings and lockable hinged doors. The enclosure is made of robust insulated panel to provide sound and thermal insulation and access around engine generator sheet steel construction.
- Ease of access for oil drain plug
| Maintenance tools | Each generating set is supplied with routine maintenance tool.
| Spare parts | Generating set will be delivered with the following spare parts:
o Air Filter
o Oil Filter
o Fuel Filter
All other manufacturer-recommended spares for two years operation
| Accessories | All necessary accessories to connect the generator ATS (Automatic Transfer switch) and CMDB (Central main distribution board).
| Operating conditions: | a) Altitude: 1000-2300 m above sea level
b) Ambient Temperature: 12 to 24°C
c) Relative Humidity : 30-60%
| Documentation | The following documents must be submitted with offer in English and French:
- Complete operator’s manual: showing standard operations and required maintenance, recommended spare parts catalogued, electrical diagrams, and troubleshooting guidance.
- Test certificate, brochures, leaflet, and catalogues that describe detail technical data.
| Warranty | One year warranty
| Testing and commissioning | Generation set is subjected to a strict load test before delivery. Test certificate shall be provided.
| Regulatory and Standards: | ISO 8528,
IEC 34.1,
CEI 2.3,
VDE0530,
BS4999-5000
NF 51-100 and is fully accredited ISO 9001 Company.
N/A
Note on B69: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @team please confirm environmental conditions at PSA sites

## RFI_MFLab (hidden)
| 关于产品 | [9 empty] | 关于贵司
产品类型 Product Type | 产品标准要求 Product Specifications | 产品型号（请列出贵公司符合左侧标准要求的产品，并邮件提供电子版产品用户手册） Product Model (s) | 产品排期（假设下周下订单，预计能够供的最早出货排期至何时（日期）？ Lead time if order placed next week (date) | 本次订单所需数量 Units Required | 公司当前可出售的数量 Units Available | 法规批准/认证Regulatory Approval/Certification |  | 产品性能标准Standards, for product performance |  | 产品单价（美金） Unit price (USD) | 制造商标准 Standards, for manufacturer |  | 预付款要求 Pre-payment requirement | 公司以前有向埃塞俄比亚出口的经验吗？Does company have previous export experience to Ethiopia? | 图片示例 Picture
[6 empty] | 标准 | 如果有，请填写 “X” | 标准 | 如果有，清填写 “X” |  | 标准 | 如果有，清填写 “X”
简单氧气气面罩 Simple Face Masks | 成人式： 医用级 | LB1110, Adult(LA), 5.5mm x 2m绿色管 |  | 2000 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X | 生产前付清 | 有
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
ISO 18190
[8 empty] | ISO18562-1 | X
ISO/DIS 23368
[8 empty] | ISO/DIS 17256 | X
[8 empty] | ISO 15223-1 | X
不重吸面罩 Oxygen Mask with reservoir bag | 成人式： 氧气浓度：支持80%至100％的氧气浓度 管长: 2m 使用标准接头；管路（氧气管线）不弯曲 材质：聚氯乙烯（PVC）； 透明；医用级 | LB1310, Adult(LA), 5.5mm x 2m绿色管 氧袋1000ml |  | 2000 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
ISO 18190
[8 empty] | ISO18562-1 | X
ISO/DIS 23368
[8 empty] | ISO/DIS 17256 | X
[8 empty] | ISO 15223-1 | X
文丘里面罩（氧浓度可调面罩） Venturi Mask | 成人式：能以8至10 L / min 的流速输送低至中等流量的氧气，特定氧浓度为30％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,31%(氧气流速6L/min±10%),白色，其他符合 |  | 300 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
| 成人式：能以10至12 L / min 的流速输送低至中等流量的氧气，特定氧浓度为40％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,40%(氧气流速8L/min±10%),粉色，其他符合 |  | 300 |  | CE | X | ISO 18190
[6 empty] | FDA | X | ISO18562-1 | X
[6 empty] | 出口许可证 | X | ISO/DIS 23368
| 成人式：能以12至15 L / min 的流速输送低至中等流量的氧气，特定氧浓度为60％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,60%(氧气流速8L/min±10%),红色，其他符合 |  | 300 |  | CE | X | ISO/DIS 17256 | X
[6 empty] | FDA | X | ISO 15223-1 | X
[6 empty] | 出口许可证 | X
非侵入性/ CPAP口罩 Non-Invasive/CPAP Masks | 入口细菌过滤器（如果适用）（至少180）。 呼气过滤器，效率高。重复使用，可以承受高级消毒和灭菌。 中等大小 | LB3041,不带细菌过滤器，全硅胶，面罩+支架+头带, M |  | 130 |  | CE |  | ISO 18562-1:2017 | X |  | ISO9001 | X
[6 empty] | FDA |  | ISO 17510:2015 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X |  |  |  | ISO14971 | X
非侵入性/ CPAP口罩 Non-Invasive/CPAP Masks | 入口细菌过滤器（如果适用）（至少180）。 呼气过滤器，效率高。重复使用，可以承受高级消毒和灭菌。 大码。 | LB3041,不带细菌过滤器，全硅胶，面罩+支架+头带，L |  | 130
气管导管 Endotracheal Tube | 管： 尺码：7。 内径：7.0mm。 外径：9.3mm。 长度：最小320mm。 接头： 近端：标准内径：15mm。 远端（适合管子）：长度：最小16mm。 袖口： 直径：24mm | LB5010C, 带囊，ID 7.0mm,其他符合 |  | 350 |  | CE | X | ISO 5361:2016 | X |  | ISO9001 | X
[6 empty] | FDA |  | ISO 10993-1:2018 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO 11135:2014 | X |  | ISO14971 | X
| 管： 尺码：7.5 内径：7.5mm。长度：最小320mm。 接头： 近端：标准内径：15mm。 远端（适合管子）：长度：最小16mm。 | LB5010C, 带囊，ID 7.5mm,其他符合 |  | 350 |  | CE | X | ISO 5361:2016 | X
[6 empty] | FDA |  | ISO 10993-1:2018 | X
[6 empty] | 出口许可证 | X | ISO 11135:2014 | X