## 1-L2G Cylinder Filling Station
Component | Specification | Meet requirement? | Type of supporting documents | Comments
Overview | Output operating with a cryopump and high-pressure vaporizer to fill compressed gas cylinders for medical oxygen service, the other output passively vaporized into a distribution network to a nearby facility.
Capacity to fill 10 J size cylinders per hour
Average run time: 8 hours per day
Fill pressure: 200 bar
Provision and installation of liquid to gas filling station equipment shall be in accordance with the proposed layout (Civils arranged by customer) *Refer to: Tab 3-Filling Station layout*
Configuration | The liquid to gas (L2G) filling station consists of the following components:
• 2 x LINDE T18V130 bulk storage tanks (supplied by customer)
→ Interconnected configuration, must be reflected in P&ID
• Cryogenic liquid oxygen (LOX) pump
• High-pressure vaporizer
• Ambient vaporizer
• Medical grade copper pipes, fittings, and accessories
→ Liquid lines are rated for cryogenic service
• Pressure reducing system
• Filling manifold complete with:
→ 40 cylinder connection points
→ Bullnose valve connection BS 341 No 3 (Oxygen)
→ Secure fastening for cylinders (e.g., chain, bracket)
→ Protection cage
• Purge compressor/vacuum to empty cylinders
Cryogenic LOX Pump | Oil lubricated reciprocating pump
Maximum Output pressure: 200 bar
≥ Duplex configuration
Vacuum jacket
Mechanism for degassing
Feed and return lines
Safety guard
Suction filter
Relief valve
Safety check / non-return valves
Low pressure seals
High-Pressure and Ambient Vaporizers | High pressure vaporizer
• Rated capacity: 100 m3/hr
• Stainless steel lined
• Rated working pressure: ≥ 200 barg
Ambient vaporizer
• Rated capacity: 75 m3/hr
• All aluminum
• Rated working pressure: ≥ 36 bar
Design /maximum allowable working temp -196°C /+50°C
Inlet and outlet flange availability: ASME B16.5, BS PR C1, EN 1092, M40x2 thread, DIN 2635
All models designed according to PED 2014/68/EU, ASME SEC.VIII DIV.I, or ANSI 831.3
System Operations | Program logic-controlled System
Touch-screen control panel in English
Integrated O2 purity analyzer and monitor for medical application, paramagnetic type (or indicate otherwise)
Displayed parameters:
• Purity Oxygen concentration [%], with +/- 1% accuracy)
• System Leakage
• Pressure indication in line and headers
• Temperature
• Overall system status and time to next service
• Cummulative operating hours
Emergency shutoff
High discharge pressure switch
Loss of prime / cavitation shutdown system
Gas leakage detection
Remote monitoring feature (optional)
Power requirements | Cryopump and high-pressure vaporizer operations: 380 volts /50 Hz (3 Phase)
Control system operations: 220 VAC / 50 Hz (Single phase)
Surge protection/suppression systems
Power meter to measure the electricity consumption of the filling station
Spares | Three (3) year spare parts kits as per recommended preventative maintenance programme clearly defined in a disaggregated list comprising part numbers, descriptions, and unit cost as well as indicating brand/model specifics by the manufacturer
Installation, testing and commissioning | Detailed description of any relevant experience of importing/suppling liquid to gas filling station equipment
Evidence of effectively managed after sales service, including but not limited to installation, testing, and commissioning, repair, warranties honored, and provision of spare parts
Pre-shipment: Certificate of quality, calibration, and inspection
On-site:
• Installation to include training on start-up, use, and preventive/curative maintenance
• Inspection, testing and commissioning should be completed
Third-party inspection:
• Conformity of installation shall be verified by Authorized Inspection Authority (AIA)
Documentation | P&ID of proposed equipment configuration (Fully labelled with Element Discription/Notes and Legend)
Hard and soft copies, in English of the following:
• Certificate of quality, calibration, and inspection
User manual, detailing:
• Protocols for operations and filling instructions
• List of procedures and equipment required for cleaning
• List of procedures and equipment for preventive maintenance
• Troubleshooting chart
Contact details of manufacturer, and authorized distributors (if applicable), and local service agents
Product and model reference (brochure)
Warranty | All components of the L2G cylinder filling station should have at least 3 years’ warranty period after commissioning that covers replacement parts and labor for any manufacturer defects
The supplier must ensure the availability of spare parts for the duration of the warranty and indicate lead times
Regulatory | PED 2014/68 EU (indicate NB) Or ASME “U” stamp
QMS | ISO 9001: Quality Management Systems - Requirements
Process or component specific performance standards (or equivalent) | EIGA 159/21: Reciprocating Cryogenic Pumps and Pump Installatoins for Oxgyen, Argon, and Nitrogen
EIGA Doc 33: Cleaning of Equipment for Oxygen Service
ISO 21011: Cryogenic vessels - Valves for cryogenic service
EIGA 200/17: The Safe Design, Manufacture, Installation, Operation and Maintenance of Valves Used in Liquid Oxygen and Cold Gaseous Oxygen Systems
ISO 23208: Cryogenic vessels – cleanliness for service (specify for LOX service)

## 2-Filling Ops & Maintenance
INSTRUCTIONS
If you currently have an operational liquid to gas filling site, please complete the following table. If you are responding to this bid solicitation as a growth opportunity, in lieu of completing the table, please attach a separate proposal that explains how you will address the component requirements listed in the table below at the proposed site. Please include timelines for planning and implementation. You may consider the following resources when writing your proposal: • HTM-02-01: United Kingdom Department of Health: Health Technical Memorandum 02-01: Medical Gas Pipeline Systems - Part A Design, Installation, Validation and Verification and Part B Operational Management • NFPA 99: National Fire Protection Association (USA): Health Care Facilities Code Handbook • EIGA DOC 99/15 Good Manufacturing Practice Guide Part 1 and Part II For Medical Gases • EIGA DOC 236/21 Best Operations Practices For Filling Plants • EIGA DOC 228/20 Use of Quality Risk Management For Preparation Of Validation Protocols For Medicinal Gas Cylinder Filling
Component | Specification | Meets requirement? (Yes/No) | Type of supporting document (select from drop down) | File name as submitted | Page No. | Comments
Volume | 10 J cylinders filled per hour
Regulatory | Proof of stringent regulatory authority (SRA) approval for medical LOX
OR
Proof of product meeting the requirements of an SRA pharmacopeia (e.g., USP, Ph Eu, BP, or IP) as shown by their specification and a sample Certificate of Analysis (CoA).
Good Manufacturing Practices(GMP) | Address of liquid to gas cylinder filling site
Certificate of Analysis (CoA) template to indicate alignment with USP, Ph Eu, Int’l Pharmacopoeia, or British Pharmacopoeia
Copy of the supplier’s license to distribute medical oxygen or license as a wholesaler of medical oxygen
Proof of GMP OR the following:
• Facility safety directives.
• If a supplier is filling industrial and medical high pressure gas cylinders, an explanation of when the product streams are separated and how contamination is prevented.
• Explanation of how a batch of medical LOX is defined.
• Validation of filling and cleaning processes.
High Pressure Gas Cylinder Filling Operations | Copies of batch documentation including CE under TPED (2010/35/EU) or ASME equivalent for the product
Evidence of interior of cylinder being cleaned and inspected for oxygen service.
Documentation of frequency of testing of cylinder integrity (e.g., 5-year hydrostatic testing).
Evidence of purging cylinder prior to filling.
Explanation of how industrial and medical oxygen cylinders are segregated and how contamination is prevented.
Evidence of use of seal for the valve stem at each fill.
Evidence of skills transfer to the operators of the filling station. (I.e. Traning report, Completion of service certificates etc)
Quality Management Systems | ISO 9001: Quality Management Systems - Requirements
Documentation | Evidence of sale of medical LOX to government body
Services Agreement | • duration up to end of warranty
Provide:
o operation capacity building programme including training schedule and content - commissioning month
o cylinder filling management and operation oversight during uptime (inclusive of proposed schedule and activities) - for 6 months post-commissioning
o schedules for planned preventive maintenance (PPM) and content for training
o define technical services ( corrective maintenance, including repair agreements)covered under service agreement, parts/kits involved and their schedule(s) - up to 3 years
o provide time for response
o provide time for availability of critical spares
• State origin and/or warehouse location of all spares

## RFI_MFLab (hidden)
| 关于产品 | [9 empty] | 关于贵司
产品类型 Product Type | 产品标准要求 Product Specifications | 产品型号（请列出贵公司符合左侧标准要求的产品，并邮件提供电子版产品用户手册） Product Model (s) | 产品排期（假设下周下订单，预计能够供的最早出货排期至何时（日期）？ Lead time if order placed next week (date) | 本次订单所需数量 Units Required | 公司当前可出售的数量 Units Available | 法规批准/认证Regulatory Approval/Certification |  | 产品性能标准Standards, for product performance |  | 产品单价（美金） Unit price (USD) | 制造商标准 Standards, for manufacturer |  | 预付款要求 Pre-payment requirement | 公司以前有向埃塞俄比亚出口的经验吗？Does company have previous export experience to Ethiopia? | 图片示例 Picture
[6 empty] | 标准 | 如果有，请填写 “X” | 标准 | 如果有，清填写 “X” |  | 标准 | 如果有，清填写 “X”
简单氧气气面罩 Simple Face Masks | 成人式： 医用级 | LB1110, Adult(LA), 5.5mm x 2m绿色管 |  | 2000 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X | 生产前付清 | 有
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
ISO 18190
[8 empty] | ISO18562-1 | X
ISO/DIS 23368
[8 empty] | ISO/DIS 17256 | X
[8 empty] | ISO 15223-1 | X
不重吸面罩 Oxygen Mask with reservoir bag | 成人式： 氧气浓度：支持80%至100％的氧气浓度 管长: 2m 使用标准接头；管路（氧气管线）不弯曲 材质：聚氯乙烯（PVC）； 透明；医用级 | LB1310, Adult(LA), 5.5mm x 2m绿色管 氧袋1000ml |  | 2000 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
ISO 18190
[8 empty] | ISO18562-1 | X
ISO/DIS 23368
[8 empty] | ISO/DIS 17256 | X
[8 empty] | ISO 15223-1 | X
文丘里面罩（氧浓度可调面罩） Venturi Mask | 成人式：能以8至10 L / min 的流速输送低至中等流量的氧气，特定氧浓度为30％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,31%(氧气流速6L/min±10%),白色，其他符合 |  | 300 |  | CE | X | ISO1712:2009 |  |  | ISO9001 | X
[6 empty] | FDA | X | ISO15001 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO18562 | X |  | ISO14971 | X
| 成人式：能以10至12 L / min 的流速输送低至中等流量的氧气，特定氧浓度为40％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,40%(氧气流速8L/min±10%),粉色，其他符合 |  | 300 |  | CE | X | ISO 18190
[6 empty] | FDA | X | ISO18562-1 | X
[6 empty] | 出口许可证 | X | ISO/DIS 23368
| 成人式：能以12至15 L / min 的流速输送低至中等流量的氧气，特定氧浓度为60％。 面罩具有可调节的鼻夹。 该套件包括连接管，湿度杯和调节阀等，调节阀用颜色编码并指示氧气的百分比 (最好黄颜色）。 | LB1220,60%(氧气流速8L/min±10%),红色，其他符合 |  | 300 |  | CE | X | ISO/DIS 17256 | X
[6 empty] | FDA | X | ISO 15223-1 | X
[6 empty] | 出口许可证 | X
非侵入性/ CPAP口罩 Non-Invasive/CPAP Masks | 入口细菌过滤器（如果适用）（至少180）。 呼气过滤器，效率高。重复使用，可以承受高级消毒和灭菌。 中等大小 | LB3041,不带细菌过滤器，全硅胶，面罩+支架+头带, M |  | 130 |  | CE |  | ISO 18562-1:2017 | X |  | ISO9001 | X
[6 empty] | FDA |  | ISO 17510:2015 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X |  |  |  | ISO14971 | X
非侵入性/ CPAP口罩 Non-Invasive/CPAP Masks | 入口细菌过滤器（如果适用）（至少180）。 呼气过滤器，效率高。重复使用，可以承受高级消毒和灭菌。 大码。 | LB3041,不带细菌过滤器，全硅胶，面罩+支架+头带，L |  | 130
气管导管 Endotracheal Tube | 管： 尺码：7。 内径：7.0mm。 外径：9.3mm。 长度：最小320mm。 接头： 近端：标准内径：15mm。 远端（适合管子）：长度：最小16mm。 袖口： 直径：24mm | LB5010C, 带囊，ID 7.0mm,其他符合 |  | 350 |  | CE | X | ISO 5361:2016 | X |  | ISO9001 | X
[6 empty] | FDA |  | ISO 10993-1:2018 | X |  | ISO13485 | X
[6 empty] | 出口许可证 | X | ISO 11135:2014 | X |  | ISO14971 | X
| 管： 尺码：7.5 内径：7.5mm。长度：最小320mm。 接头： 近端：标准内径：15mm。 远端（适合管子）：长度：最小16mm。 | LB5010C, 带囊，ID 7.5mm,其他符合 |  | 350 |  | CE | X | ISO 5361:2016 | X
[6 empty] | FDA |  | ISO 10993-1:2018 | X
[6 empty] | 出口许可证 | X | ISO 11135:2014 | X