## Sheet1
INVITATION TO TENDER FOR THE DESIGN , SUPPLY AND INSTALLATION OF MEDICAL OXYGEN TELEMETRY SYSTEMS AT DESIGNATED PUBLIC HEALTH FACILITIES IN ESWATINI
OxyTel/ESW/1024 | Closing Date: 15 November 2024, 12-MIDNIGHT SAST
Frequently Asked Questions (FAQs)
Clarification Requested | Response
How long is the minimum reporting period on the digital dashboards of the system ? | The data shall be available for a minumum of five (5) years.
What are the measured parameters and their respecitve reporting times | VIE Tank pressure (real time ) , VIE Tank Level (Hourly) , MGPS Oxygen Pressure (Real time), MGPS Oxygen Flow (Real time) , MGPS Oxygen Cummulative Consumption (Hour and aboce) and MGPS Concentration / Purity (Real time)
Is Temperature part of the required parameters ? | Pressre status of the VIE Tank will indicate possible VIE Tank insulaltion challenges. Cost considerations show that there may not be need to directly meausure temperature.
What are the expectations in terms of the local display of the telemetry system ? | The local display shall be accessible to the local facility team and show all measured parameters in real time. Audio-Visual alarms are to installed and accessible as well.
Annex A shows that a registration with the Construction Industry Council is mandatory. What happens with vendors from outside Eswatini ? | Vendors from outside Eswatini shall provide the equivaletent registration papers from the respectibe country.
What are the pipe sizes on the measuring points ? | The MGPS circuits are made up of different sized pipes and these vary based on the size of the wards and oxygen demand at that particular space
Is there a need for a VIE Tank telemetry system at RFM ? | The current tank has a telematic unit but vendors need to design how to incoporate it into the new digital system
Can the vendor install new impulse lines on the VIE Tank | No, the vendor will use the existing impulse lines for the VIE Telemetry sensor connections
Is the dashboard supposed to show all facilities or each facility will have its own dashboard ? | The dashboards must show all facilities and must provide filter function based on time, facility and zone. Both the VIE Tank and MGPS Telemetry system must report on a single dashboard.
Are we allowed to use the current trenches for cabling | Trenches can be used for cabling , however all the fire safety and recommended cabling codes must be oserved
Is it mandatory to attend all site visits | All site visits are compulsory , However communication may be made and justification provided for failure to attend the site briefings
Do all the the VIE Tanks have pre-installed gauges | The tanks do have pre-installed Analogue gauges. The Microbulk tanks also have pressure transmitters with them. It shall be the vendors responsibilty to test and determine if the transmitters are functional
What is the recommended trucking for cables ? | Cabling shall be done as specified in the Annexes , taking into consideration the IP index in each case.
Can the Vendor use the available power sources installed at the VIE Tank sites ? | Power sources at the sites can be used for installation and shall be considered during design of the telemetry solutions
Can the P&IDs for the Medical Gas Piping Circuits be provided ? | There are currently no P&IDs for the circuits. The vendor shall work closely with the facility Biomed Engineers / Technicians to trace the oxygen circuits
Can the hospital facility layout plans be availed to vendors ? | The CHAI team will work with the facility planning departments to request the hospital building and layout plans.
Can the VIE Tank dimensions be shared with the vendors ? | Dimensions of tanks are available in data sheets and they will be made available to the successful bidder.