## Summary
SUMMARY
| REFERENCE NUMBER | CIVIL WORKS - RFP/CHAI-TZ-EPIC-001/25
Item | Healthcare Facility | Total Tshs | Delivery Period in Days | Comments
1 | Muhimbili National Hospital | 0
2 | Mwananyamala Regional Referral Hospital | 0
3 | Muhimbili Orthopedic Institute | 0
4 | Temeke Regional Referral Hospital | 0
| Total in Tanzanian Shillings | 0

## MNH
BILLS OF QUANTITIES [BOQs]
CIVIL WORKS - RFP/CHAI-TZ-EPIC-CIVIL 001/25
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
PREAMBLES
A1 | The project will include six (6) main tasks namely; i) Reinforced concrete plinth to support the 30t-VIE-Tank; ii) Palisade fencing around three-sides of the plinth perimeter; iii) Solid-concrete-blocks wall on one side of the plinth perimeter and, Paving-blocks Apron around the plinth-perimeter; iv) Electrical installations that include 3-phase-power-socket and, 2-security-lights fixed on steel-poles; v) Tap-water near oxygen-tank for de-icing of valves or to handle emergency situations; vi) Fire-fighting-system (Hydrant-Outlet)
A2 | Engagement of Registered Building Contractor by Contractors Registration Board (CRB) is inavitable also, a specialist domestic Electrical Sub-contractor is necessary for appropriate sketch and implementation of power and security-lights
A3 | The VIE-Tank will be supplied and installed by other Vendor; but, she will also supply the Anchor-Bolts to be embedded in the reinforced concrete slab by you as per the Drawings; joint-consultation-and-coordination are required;
A4 | Anchor-Bolts for Vaporizers will be supplied and fixed in reinforced concrete slab complete with washers by you;
A5 | The Fire-fighting-system (Hydrant-Output) allowance is provisional subject to the outcome of the tender; as-built-sketches will be required before commissioning;
A6 | The site is within the Muhimbili National Hospital (MNH) in DAR ES SALAAM City; about 12m behind Maternity-Ward-II, located next to PSA-plant and side of Pediatric-Ward;
PRELIMINARIES
B1 | By-Laws | 1 | Item |  | 0
B2 | Power for the works | 1 | Item |  | 0
B3 | Water for the works | 1 | Item |  | 0
B4 | Plants such as Concrete-Mixer, Plate-Compactor; Working-tools such as ladders; and the like; | 1 | Item |  | 0
B5 | Transport for materials | 1 | Item |  | 0
B6 | Construction management | 1 | Item |  | 0
B7 | Mix-Design for Reinforced Concrete Grade-30 | 1 | Item |  | 0
B8 | Testing of Materials (sand; aggregates; reinforcements; water) and Components (concrete-cubes; solid-blocks/bricks) | 1 | Item |  | 0
B9 | Cleaning the site for commissioning; | 1 | Item |  | 0
B10 | Signage | 1 | Item |  | 0
B11 | Safety-gears | 1 | Item |  | 0
B12 | UPVC-4" Pipe; for all services from the tank; | 1 | Item |  | 0
1 | DEMOLITIONS AND ALTERATIONS
1.1 | Cut the existing 1-tree 200-300mm girth; | 1 | Item |  | 0
1.2 | Cut and remove two dislocated concrete slabs; approximately 12m2; dispose debries away from site; | 1 | Item |  | 0
2 | EXCAVATION AND EARTHWORK
Site preparation
2.1 | Excavate Oversite average 300mm deep to remove vegetable soil load up wheel and cart away | 81 | M2 |  | 0 |  | 88 | 10 | 7 | 4.49 | 2.5 | 81.225
General excavation
Trenches excavation
2.2 | Excavate to reduce levels not exceeding 1.5m deep from stripped level | 122 | M3 |  | 0 |  | 121.8375
Backfilling excavated materials
2.3 | Level and compact surface of excavation or filling in layers not exceeding 200mm thick | 101 | M3 |  | 0
Surplus excavated material
2.4 | load up and remove surplus excavated material to stockpile on/off site not exceeding 40km distance | 21 | M3 |  | 0 |  | 20 | 0.56025 | 20.5602 | 20.5602
Imported Sand; deposited and compacted in layers granular fill compacted in 150mm layers to 95% maximum dry density (m.d.d)
2.5 | Around foundations | 10 | M3 |  | 0 |  | 7.8 | 1.647 | 9.447
2.6 | On top of hardcore | 3 | M3 |  | 0 |  | 60.775 | 3.0387
Plunking and Strutting
2.7 | Allow for planking and strutting to sides of excavations | 1 | Item |  | 0
Disposal of Water
2.8 | Allow for keeping excavations free from mud and all water including spring and running water by pumbing pailing and other approved means | 1 | Item |  | 0
Blinding; Grade 10 (nominal mix 1:3:6; 15N/mm2 at 28 days)
2.9 | 50mm thick to receive hardcore bed (m.s.) | 61 | M2 |  | 0 |  | 60.775
Hardcore Bed
2.1 | 200mm thick layer approved hardcore filling well watered, rolled and compacted in layers not exceeding 150mm thick under floors to level and slope as required | 61 | M2 |  | 0
Soil Sterilization
2.11 | TERMIDOR 25EC' or other equal and approved chemical anti-termitr treatment to top surfaces of sand-blinded hardcore | 61 | M2 |  | 0
Damp Proof Membrane (DPM)
2.12 | 1000 gauge polythene damp-proof sheeting laid on blinded smooth finished hardcore bed with 300mm side and end laps to receive conrete bed (m.s) | 61 | M2 |  | 0
In-situ Reinforced Concrete; Raft-Foundation; Grade 30
2.13 | 500mm thick floor slab | 40 | M2 |  | 0 | 40
2.14 | 150mm thick Ramp; sloping not exceeding 45° from horizontal; | 4 | M2 |  | 0 | 4.707
2.15 | Ground beam | 3 | M3 |  | 0 | 3.0144
Reinforcement including bends, hooks, tying wires, distant blocks and ordinary spacers; Hot Rolled; High Yield Steel Bars BS 4449 - Assorted sizes as per the drawings; High Yield Strength 460MPa; Cutting and Bending as per BS 8666; to slabs and beams (Provisional)
2.16 | Y20 | 323 | Kg |  | 0
2.17 | Y16 | 323 | Kg |  | 0
2.18 | Y12 | 200 | Kg |  | 0
2.19 | Y10 | 11 | Kg |  | 0
2.2 | Assorted sizes (provisional) | 150 | Kg |  | 0
Sawn Formwork; vertical or battering surfaces
2.21 | Edges of ground-beams; 500mm girth | 26 | M |  | 0 | 26 |  | 5.49
2.22 | Ditto; 150mm girth | 6 | M |  | 0
Plinth Finishing
2.23 | 12mm thick cement sand mix (1:3) plastering; 3mm thick stucco or equal and approved surface well lied with steel trowelled finish on concrete surfaces | 14 | M2 |  | 0 | 13.8235
2.24 | Prepare and apply three coats of black bituminous paint to rendered surfaces of plinths | 14 | M2 |  | 0
Floor Finish
2.25 | 32mm thick cement sand mix (1:3) screed well lied with steel-trowelled finish; | 44 | M2 |  | 0
Holding Down Anchor Bolts
2.26 | Tank to be anchored down using HILTI-Chemical-Anchors (to be supplied and specified by tank manufacturer) to be appropriately embedded in the reinforced-concrete-slab; with minimum of 2-anchor-bolts in each-leg making 6-anchor-bolts; as per the drawings | 1 | Item |  | 0
2.27 | Supply and fix rectangular-hollow-sections; 75x75x2.5mm, 2400mm high, main members; including 300mm deep embedded in reinforced concrete slab; | 12 | Nr |  | 0
2.28 | Supply and fix Anchor-bolts complete with washels to receive Vaporiser (to be supplied and specified by manufacturer) | 1 | Item |  | 0
Foundation Apron around plinth-perimeter
2.29 | 600x600x50mm; Concrete-Paving-Slabs around | 14 | M2 |  | 0 | 15.6 | 1.494 | 14.106
3 | FENCING (SOLID BLOCKWORK AND PELISADE)
3.1 | 230mm thick Solid cement-sand blocks with strength of 4.5MPa: bedded and jointed in cement/sand mortar(1:4): external | 15 | M2 |  | 0 | 15.072 | 640
3.2 | Plastering internal; 12mm thick mix 1:3) cement sand plaster; 3mm thick stucco or equal and approved to masonry-walling | 30 | M2 |  | 0 | 15.072
3.3 | 230x400mm In-situ reinforced concrete Beam Grade-30 including necessary shuttering | 1 | M3 |  | 0 | 0.57776
Roofing (provisional)
3.4 | Supply and fabricate; welded and socketed; 50x50x4mm Mild-steel Angle Section Trusses and Purlins; apply two coats of anti-rust-paint and; one finishing gloss-oil-paint; | 32 | M |  | 0 | 15.708 | 914 | 3.656 | 19.364 | 12.4 | 31.764
3.5 | Supply gauge 26 gauge IT5 Resincoated Alu-zink roof sheets including self-drilling screws and fix to metal purlins. | 12 | M2 |  | 0 | 12.028
3.6 | Supply and fix gauge 26 resincoated plain-sheets welded to 375mm Barge; | 6 | M |  | 0 | 6.2
3.7 | Supply and fix gauge 26 resincoated plain-sheets welded to 100mm Fascia; | 6 | M |  | 0
3.8 | 300mm girth Metal Gutter 6m long complete with clips and one down-pipe 2.4 high; | 1 | Item |  | 0
Palisade Fence
3.9 | Supply and fix palisade fence; 2100mm high, robust vertical rectangular hollow sections 25x25x1.5mm, infill-materials; complete with 25x25x1.5mm 3-horizontal-bracings; | 15 | M |  | 0 | 16
3.1 | Supply and fix; 300mm high razor-wire with its tension-wire; on top of fence, gate and door; | 15 | M |  | 0 | 6900 | 12.87 | 2.28 | 15.15
Gate and Emergency Door
3.11 | Supply and fix; Double-Leafs; 2490mm wide x 2100mm high overall palisade gate comprising of robust vertical steel pales secured to horizonal rails, including all necessary iron mongery i.e hasps and staple and applying one coat red oxide primer before delivery to site and handing gate to posts (m.s.) | 1 | Nr |  | 0
3.12 | Supply and fix; 930mm wide x 2100mmhigh overall palisade emergency-door comprising of robust vertical steel pales secured to horizonal rails, including all necessary iron mongery i.e hasps and staple and applying one coat red oxide primer before delivery to site and handing gate to posts (m.s.) | 1 | Nr |  | 0
4 | PAINTING
Prepare and apply to surfaces; spray three coats of gloss-oil-paint on;
4.1 | Palisade surfaces; internal and external | 32 | M2 |  | 0 | 31.5
4.2 | Gate surfaces; ditto; | 5 | M2 |  | 0 | 5.229
4.3 | Emergency-Door surfaces; ditto | 2 | M2 |  | 0 | 1.953
Prepare and apply; three-coats of weather-guard paints on;
4.4 | Plastered wall surfaces | 30 | M2 |  | 0
5 | POWER SUPPLY
5.1 | Electricity 3 Phase, supply and fix; armored cable (4mmx3core), about 18m in the ground, 5m up to dB in the Maternity-ward-II; including excavation and backfilling, UPVC-Class-B-100mmΦ for underground-cable; complete with dB, Industrial-Switch-Socket-Outlet, cables and all necessary accessories; | 1 | Item |  | 0
5.2 | Supply and fix; Security Lights-250W; complete with 50mmΦ steel-poles; complete with cables, photocell-switch and all necessary accessories; | 2 | Nr |  | 0
6 | WATER-NETWORK
6.1 | Supply and fix; appropriate 1-Water-tap; 32mm OD HDPE pipe, PE 100 PN 10 with all accessories and pipe-fittings for emergency water use when required like defrezing from the source which is about 15m away in the ground; | 1 | Item |  | 0
6.2 | Supply and install 1-in-No 100mm norminal diameter underground / pillar fire hydrant with two outlets of 65mm, type "ANGUS" or similar to be approved; Supply and lay fire hydrant pipes 100mm diameter 15m-long including excavating, backfilling, elbows, bends and any other associated accessories. (Minimum cover); Supply and install 2-in-No 100mm diameter stop valve for fire hydrant water supply main. | 1 | Item |  | 0
| SUB-TOTAL |  |  |  | 0
| VAT-18% |  |  |  | 0
| TOTAL |  |  |  | 0

## MRRH
BILLS OF QUANTITIES [BOQs]
CIVIL WORKS - RFP/CHAI-TZ-EPIC-CIVIL 001/25
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
PREAMBLES
A1 | The project will include six (6) main tasks namely; i) Reinforced concrete plinth to support the 10t-VIE-Tank; ii) Palisade fencing around three-sides of the plinth perimeter; iii) Solid-concrete-blocks wall on one side of the plinth perimeter and, Paving-blocks Apron around the plinth-perimeter; iv) Electrical installations that include 3-phase-power-socket and, 2-security-lights fixed on steel-poles; v) Tap-water near oxygen-tank for de-icing of valves or to handle emergency situations; vi) Fire-fighting-system (Hydrant-Outlet)
A2 | Engagement of Registered Building Contractor by Contractors Registration Board (CRB) is inavitable also, a specialist domestic Electrical Sub-contractor is necessary for appropriate sketch and implementation of power and security-lights
A3 | The VIE-Tank will be supplied and installed by other Vendor; but, she will also supply the Anchor-Bolts to be embedded in the reinforced concrete slab by you as per the Drawings; joint-consultation-and-coordination are required;
A4 | Anchor-Bolts for Vaporizers will be supplied and fixed in reinforced concrete slab complete with washers by you;
A5 | The Fire-fighting-system (Hydrant-Output) allowance is provisional subject to the outcome of the tender; as-built-sketches will be required before commissioning;
A6 | The site is within the Mwananyamala Regional Referral Hospital (MRRH) in DAR ES SALAAM City; about 17m behind Maternity-Ward;
PRELIMINARIES
B1 | By-Laws | 1 | Item |  | 0
B2 | Power for the works | 1 | Item |  | 0
B3 | Water for the works | 1 | Item |  | 0
B4 | Plants such as Concrete-Mixer, Plate-Compactor; Working-tools such as ladders; and the like; | 1 | Item |  | 0
B5 | Transport for materials | 1 | Item |  | 0
B6 | Construction management | 1 | Item |  | 0
B7 | Mix-Design for Reinforced Concrete Grade-30 | 1 | Item |  | 0
B8 | Testing of Materials (sand; aggregates; reinforcements; water) and Components (concrete-cubes; solid-blocks/bricks) | 1 | Item |  | 0
B9 | Cleaning the site for commissioning; | 1 | Item |  | 0
B10 | Signage | 1 | Item |  | 0
B11 | Safety-gears | 1 | Item |  | 0
B12 | UPVC-4" Pipe; for all services from the tank; | 1 | Item |  | 0
1 | DEMOLITIONS AND ALTERATIONS
1.1 | Presence of two existing soak/placenta pits that are about 2500mm Ø requiring filling and demolition; | 1 | Item |  | 0
2 | EXCAVATION AND EARTHWORK
Site preparation
2.1 | Excavate Oversite average 300mm deep to remove vegetable soil load up wheel and cart away | 60 | M2 |  | 0 |  |  | 7 | 7 | 4.49 | 2.5 | 60.225
General excavation
Trenches excavation
2.2 | Excavate to reduce levels not exceeding 1.5m deep from stripped level | 90 | M3 |  | 0 |  | 90.3375
Backfilling excavated materials
2.3 | Level and compact surface of excavation or filling in layers not exceeding 200mm thick | 77 | M3 |  | 0
Surplus excavated material
2.4 | load up and remove surplus excavated material to stockpile on/off site not exceeding 40km distance | 13 | M3 |  | 0 |  | 12.5 | 0.56025 | 13.0602 | 13.0602
Imported Sand; deposited and compacted in layers granular fill compacted in 150mm layers to 95% maximum dry density (m.d.d)
2.5 | Around foundations | 8 | M3 |  | 0 |  | 6 | 1.647 | 7.647
2.6 | On top of hardcore | 2 | M3 |  | 0 |  | 42.175 | 2.1088
Plunking and Strutting
2.7 | Allow for planking and strutting to sides of excavations | 1 | Item |  | 0
Disposal of Water
2.8 | Allow for keeping excavations free from mud and all water including spring and running water by pumbing pailing and other approved means | 1 | Item |  | 0
Blinding; Grade 10 (nominal mix 1:3:6; 15N/mm2 at 28 days)
2.9 | 50mm thick to receive hardcore bed (m.s.) | 42 | M2 |  | 0 |  | 42.175
Hardcore Bed
2.1 | 200mm thick layer approved hardcore filling well watered, rolled and compacted in layers not exceeding 150mm thick under floors to level and slope as required | 42 | M2 |  | 0
Soil Sterilization
2.11 | TERMIDOR 25EC' or other equal and approved chemical anti-termitr treatment to top surfaces of sand-blinded hardcore | 42 | M2 |  | 0
Damp Proof Membrane (DPM)
2.12 | 1000 gauge polythene damp-proof sheeting laid on blinded smooth finished hardcore bed with 300mm side and end laps to receive conrete bed (m.s) | 42 | M2 |  | 0
In-situ Reinforced Concrete; Raft-Foundation; Grade 30
2.13 | 500mm thick floor slab | 25 | M2 |  | 0 | 25
2.14 | 150mm thick Ramp; sloping not exceeding 45° from horizontal; | 5 | M2 |  | 0 | 4.707
2.15 | Ground beam | 2 | M3 |  | 0 | 2.3244
Reinforcement including bends, hooks, tying wires, distant blocks and ordinary spacers; Hot Rolled; High Yield Steel Bars BS 4449 - Assorted sizes as per the drawings; High Yield Strength 460MPa; Cutting and Bending as per BS 8666; to slabs and beams (Provisional)
2.16 | Y20 | 323 | Kg |  | 0
2.17 | Y16 | 323 | Kg |  | 0
2.18 | Y12 | 200 | Kg |  | 0
2.19 | Y10 | 11 | Kg |  | 0
2.2 | Assorted sizes (provisional) | 100 | Kg |  | 0
Sawn Formwork; vertical or battering surfaces
2.21 | Edges of ground-beams; 500mm girth | 32 | M |  | 0 | 20 |  | 5.49
2.22 | Ditto; 150mm girth | 6 | M |  | 0
Plinth Finishing
2.23 | 12mm thick cement sand mix (1:3) plastering; 3mm thick stucco or equal and approved surface well lied with steel trowelled finish on concrete surfaces | 11 | M2 |  | 0 | 10.8235
2.24 | Prepare and apply three coats of black bituminous paint to rendered surfaces of plinths | 11 | M2 |  | 0
Floor Finish
2.25 | 32mm thick cement sand mix (1:3) screed well lied with steel-trowelled finish; | 30 | M2 |  | 0
Holding Down Anchor Bolts
2.26 | Tank to be anchored down using HILTI-Chemical-Anchors (to be supplied and specified by tank manufacturer) to be appropriately embedded in the reinforced-concrete-slab; with minimum of 2-anchor-bolts in each-leg making 6-anchor-bolts; as per the drawings | 1 | Item |  | 0
2.27 | Supply and fix rectangular-hollow-sections; 75x75x2.5mm, 2400mm high, main members; including 300mm deep embedded in reinforced concrete slab; | 10 | Nr |  | 0
2.28 | Supply and fix Anchor-bolts complete with washels to receive Vaporiser (to be supplied and specified by manufacturer) | 1 | Item |  | 0
Foundation Apron around plinth-perimeter
2.29 | 600x600x50mm; Concrete-Paving-Slabs around | 11 | M2 |  | 0 | 12 | 1.494 | 10.506
3 | FENCING (SOLID BLOCKWORK AND PELISADE)
3.1 | 230mm thick Solid cement-sand blocks with strength of 4.5MPa: bedded and jointed in cement/sand mortar(1:4): external | 15 | M2 |  | 0 | 15.072 | 640
3.2 | Plastering internal; 12mm thick mix 1:3) cement sand plaster; 3mm thick stucco or equal and approved to masonry-walling | 30 | M2 |  | 0 | 15.072
3.3 | 230x400mm In-situ reinforced concrete Beam Grade-30 including necessary shuttering | 1 | M3 |  | 0 | 0.57776
Roofing (provisional)
3.4 | Supply and fabricate; welded and socketed; 50x50x4mm Mild-steel Angle Section Trusses and Purlins; apply two coats of anti-rust-paint and; one finishing gloss-oil-paint; | 32 | M |  | 0 | 15.708 | 914 | 3.656 | 19.364 | 12.4 | 31.764
3.5 | Supply gauge 26 gauge IT5 Resincoated Alu-zink roof sheets including self-drilling screws and fix to metal purlins. | 12 | M2 |  | 0 | 12.028
3.6 | Supply and fix gauge 26 resincoated plain-sheets welded to 375mm Barge; | 6 | M |  | 0 | 6.2
3.7 | Supply and fix gauge 26 resincoated plain-sheets welded to 100mm Fascia; | 6 | M |  | 0
3.8 | 300mm girth Metal Gutter 6m long complete with clips and one down-pipe 2.4 high; | 1 | Item |  | 0
Palisade Fence
3.9 | Supply and fix palisade fence; 2100mm high, robust vertical rectangular hollow sections 25x25x1.5mm, infill-materials; complete with 25x25x1.5mm 3-horizontal-bracings; | 9 | M |  | 0
3.1 | Supply and fix; 300mm high razor-wire with its tension-wire; on top of fence, gate and door; | 9 | M |  | 0 | 7800 | 0.93 | 2.28 | 10.08 | 9.15
Gate and Emergency Door
3.11 | Supply and fix; Double-Leafs; 2490mm wide x 2100mm high overall palisade gate comprising of robust vertical steel pales secured to horizonal rails, including all necessary iron mongery i.e hasps and staple and applying one coat red oxide primer before delivery to site and handing gate to posts (m.s.) | 1 | Nr |  | 0
3.12 | Supply and fix; 930mm wide x 2100mmhigh overall palisade emergency-door comprising of robust vertical steel pales secured to horizonal rails, including all necessary iron mongery i.e hasps and staple and applying one coat red oxide primer before delivery to site and handing gate to posts (m.s.) | 1 | Nr |  | 0
4 | PAINTING
Prepare and apply to surfaces; spray three coats of gloss-oil-paint on;
4.1 | Palisade surfaces; internal and external | 19 | M2 |  | 0 | 18.9
4.2 | Gate surfaces; ditto; | 5 | M2 |  | 0 | 5.229
4.3 | Emergency-Door surfaces; ditto | 2 | M2 |  | 0 | 1.953
Prepare and apply; three-coats of weather-guard paints on;
4.4 | Plastered wall surfaces | 30 | M2 |  | 0
5 | POWER SUPPLY
5.1 | Electricity 3 Phase, supply and fix; armored cable (4mmx3core), about 82m in the ground, 5m up to dB; including excavation and backfilling, UPVC-Class-B-100mmΦ for underground-cable; complete with dB, Industrial-Switch-Socket-Outlet, cables and all necessary accessories; | 1 | Item |  | 0
5.2 | Supply and fix; Security Lights-250W; complete with 50mmΦ steel-poles; complete with cables, photocell-switch and all necessary accessories; | 2 | Nr |  | 0
6 | WATER-NETWORK
6.1 | Supply and fix; appropriate 1-Water-tap; 32mm OD HDPE pipe, PE 100 PN 10 with all accessories and pipe-fittings for emergency water use when required like defrezing from the source which is about 27m away in the ground; | 1 | Item |  | 0
6.2 | Supply and install 1-in-No 100mm norminal diameter underground / pillar fire hydrant with two outlets of 65mm, type "ANGUS" or similar to be approved; Supply and lay fire hydrant pipes 100mm diameter 27m-long including excavating, backfilling, elbows, bends and any other associated accessories. (Minimum cover); Supply and install 2-in-No 100mm diameter stop valve for fire hydrant water supply main. | 1 | Item |  | 0
| SUB-TOTAL |  |  |  | 0
| VAT-18% |  |  |  | 0
| TOTAL |  |  |  | 0

## MOI
BILLS OF QUANTITIES [BOQs]
CIVIL WORKS - RFP/CHAI-TZ-EPIC-CIVIL 001/25
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
PREAMBLES
A1 | The project will include six (6) main tasks namely; i) Reinforced concrete plinth to support the 10t-VIE-Tank; ii) Palisade fencing around three-sides of the plinth perimeter; iii) Solid-concrete-blocks wall on one side of the plinth perimeter and, Paving-blocks Apron around the plinth-perimeter; iv) Electrical installations that include 3-phase-power-socket and, 2-security-lights fixed on steel-poles; v) Tap-water near oxygen-tank for de-icing of valves or to handle emergency situations; vi) Fire-fighting-system (Hydrant-Outlet)
A2 | Engagement of Registered Building Contractor by Contractors Registration Board (CRB) is inavitable also, a specialist domestic Electrical Sub-contractor is necessary for appropriate sketch and implementation of power and security-lights
A3 | The VIE-Tank will be supplied and installed by other Vendor; but, she will also supply the Anchor-Bolts to be embedded in the reinforced concrete slab by you as per the Drawings; joint-consultation-and-coordination are required;
A4 | Anchor-Bolts for Vaporizers will be supplied and fixed in reinforced concrete slab complete with washers by you;
A5 | The Fire-fighting-system (Hydrant-Output) allowance is provisional subject to the outcome of the tender; as-built-sketches will be required before commissioning;
A6 | The Muhimbili Orthopedic Institute (MOI) is within MNH and, the site for Liquid Oxygen Tank is opposite to MOI-03 – Building across the road adjacent to PSA-plant in DAR ES SALAAM City;
PRELIMINARIES
B1 | By-Laws | 1 | Item |  | 0
B2 | Power for the works | 1 | Item |  | 0
B3 | Water for the works | 1 | Item |  | 0
B4 | Plants such as Concrete-Mixer, Plate-Compactor; Working-tools such as ladders; and the like; | 1 | Item |  | 0
B5 | Transport for materials | 1 | Item |  | 0
B6 | Construction management | 1 | Item |  | 0
B7 | Mix-Design for Reinforced Concrete Grade-30 | 1 | Item |  | 0
B8 | Testing of Materials (sand; aggregates; reinforcements; water) and Components (concrete-cubes; solid-blocks/bricks) | 1 | Item |  | 0
B9 | Cleaning the site for commissioning; | 1 | Item |  | 0
B10 | Signage | 1 | Item |  | 0
B11 | Safety-gears | 1 | Item |  | 0
B12 | UPVC-4" Pipe; for all services from the tank; | 1 | Item |  | 0
1 | DEMOLITIONS AND ALTERATIONS
1.1 | Presence of existing mango-tree for pruning and; dispose debris away from site; | 1 | Item |  | 0
2 | EXCAVATION AND EARTHWORK
Site preparation
2.1 | Excavate Oversite average 300mm deep to remove vegetable soil load up wheel and cart away | 60 | M2 |  | 0 |  |  | 7 | 7 | 4.49 | 2.5 | 60.225
General excavation
Trenches excavation
2.2 | Excavate to reduce levels not exceeding 1.5m deep from stripped level | 90 | M3 |  | 0 |  | 90.3375
Backfilling excavated materials
2.3 | Level and compact surface of excavation or filling in layers not exceeding 200mm thick | 77 | M3 |  | 0
Surplus excavated material
2.4 | load up and remove surplus excavated material to stockpile on/off site not exceeding 40km distance | 13 | M3 |  | 0 |  | 12.5 | 0.56025 | 13.0602 | 13.0602
Imported Sand; deposited and compacted in layers granular fill compacted in 150mm layers to 95% maximum dry density (m.d.d)
2.5 | Around foundations | 8 | M3 |  | 0 |  | 6 | 1.647 | 7.647
2.6 | On top of hardcore | 2 | M3 |  | 0 |  | 42.175 | 2.1088
Plunking and Strutting
2.7 | Allow for planking and strutting to sides of excavations | 1 | Item |  | 0
Disposal of Water
2.8 | Allow for keeping excavations free from mud and all water including spring and running water by pumbing pailing and other approved means | 1 | Item |  | 0
Blinding; Grade 10 (nominal mix 1:3:6; 15N/mm2 at 28 days)
2.9 | 50mm thick to receive hardcore bed (m.s.) | 42 | M2 |  | 0 |  | 42.175
Hardcore Bed
2.1 | 200mm thick layer approved hardcore filling well watered, rolled and compacted in layers not exceeding 150mm thick under floors to level and slope as required | 42 | M2 |  | 0
Soil Sterilization
2.11 | TERMIDOR 25EC' or other equal and approved chemical anti-termitr treatment to top surfaces of sand-blinded hardcore | 42 | M2 |  | 0
Damp Proof Membrane (DPM)
2.12 | 1000 gauge polythene damp-proof sheeting laid on blinded smooth finished hardcore bed with 300mm side and end laps to receive conrete bed (m.s) | 42 | M2 |  | 0
In-situ Reinforced Concrete; Raft-Foundation; Grade 30
2.13 | 500mm thick floor slab | 25 | M2 |  | 0 | 25
2.14 | 150mm thick Ramp; sloping not exceeding 45° from horizontal; | 5 | M2 |  | 0 | 4.707
2.15 | Ground beam | 2 | M3 |  | 0 | 2.3244
Reinforcement including bends, hooks, tying wires, distant blocks and ordinary spacers; Hot Rolled; High Yield Steel Bars BS 4449 - Assorted sizes as per the drawings; High Yield Strength 460MPa; Cutting and Bending as per BS 8666; to slabs and beams (Provisional)
2.16 | Y20 | 323 | Kg |  | 0
2.17 | Y16 | 323 | Kg |  | 0
2.18 | Y12 | 200 | Kg |  | 0
2.19 | Y10 | 11 | Kg |  | 0
2.2 | Assorted sizes (provisional) | 100 | Kg |  | 0
Sawn Formwork; vertical or battering surfaces
2.21 | Edges of ground-beams; 500mm girth | 32 | M |  | 0 | 20 |  | 5.49
2.22 | Ditto; 150mm girth | 6 | M |  | 0
Plinth Finishing
2.23 | 12mm thick cement sand mix (1:3) plastering; 3mm thick stucco or equal and approved surface well lied with steel trowelled finish on concrete surfaces | 11 | M2 |  | 0 | 10.8235
2.24 | Prepare and apply three coats of black bituminous paint to rendered surfaces of plinths | 11 | M2 |  | 0
Floor Finish
2.25 | 32mm thick cement sand mix (1:3) screed well lied with steel-trowelled finish; | 30 | M2 |  | 0
Holding Down Anchor Bolts
2.26 | Tank to be anchored down using HILTI-Chemical-Anchors (to be supplied and specified by tank manufacturer) to be appropriately embedded in the reinforced-concrete-slab; with minimum of 2-anchor-bolts in each-leg making 6-anchor-bolts; as per the drawings | 1 | Item |  | 0
2.27 | Supply and fix rectangular-hollow-sections; 75x75x2.5mm, 2400mm high, main members; including 300mm deep embedded in reinforced concrete slab; | 10 | Nr |  | 0
2.28 | Supply and fix Anchor-bolts complete with washels to receive Vaporiser (to be supplied and specified by manufacturer) | 1 | Item |  | 0
Foundation Apron around plinth-perimeter
2.29 | 600x600x50mm; Concrete-Paving-Slabs around | 11 | M2 |  | 0 | 12 | 1.494 | 10.506
3 | FENCING (SOLID BLOCKWORK AND PELISADE)
3.1 | 230mm thick Solid cement-sand blocks with strength of 4.5MPa: bedded and jointed in cement/sand mortar(1:4): external | 15 | M2 |  | 0 | 15.072 | 640
3.2 | Plastering internal; 12mm thick mix 1:3) cement sand plaster; 3mm thick stucco or equal and approved to masonry-walling | 30 | M2 |  | 0 | 15.072
3.3 | 230x400mm In-situ reinforced concrete Beam Grade-30 including necessary shuttering | 1 | M3 |  | 0 | 0.57776
Roofing (provisional)
3.4 | Supply and fabricate; welded and socketed; 50x50x4mm Mild-steel Angle Section Trusses and Purlins; apply two coats of anti-rust-paint and; one finishing gloss-oil-paint; | 32 | M |  | 0 | 15.708 | 914 | 3.656 | 19.364 | 12.4 | 31.764
3.5 | Supply gauge 26 gauge IT5 Resincoated Alu-zink roof sheets including self-drilling screws and fix to metal purlins. | 12 | M2 |  | 0 | 12.028
3.6 | Supply and fix gauge 26 resincoated plain-sheets welded to 375mm Barge; | 6 | M |  | 0 | 6.2
3.7 | Supply and fix gauge 26 resincoated plain-sheets welded to 100mm Fascia; | 6 | M |  | 0
3.8 | 300mm girth Metal Gutter 6m long complete with clips and one down-pipe 2.4 high; | 1 | Item |  | 0
Palisade Fence
3.9 | Supply and fix palisade fence; 2100mm high, robust vertical rectangular hollow sections 25x25x1.5mm, infill-materials; complete with 25x25x1.5mm 3-horizontal-bracings; | 9 | M |  | 0
3.1 | Supply and fix; 300mm high razor-wire with its tension-wire; on top of fence, gate and door; | 9 | M |  | 0 | 7800 | 0.93 | 2.28 | 10.08 | 9.15
Gate and Emergency Door
3.11 | Supply and fix; Double-Leafs; 2490mm wide x 2100mm high overall palisade gate comprising of robust vertical steel pales secured to horizonal rails, including all necessary iron mongery i.e hasps and staple and applying one coat red oxide primer before delivery to site and handing gate to posts (m.s.) | 1 | Nr |  | 0
3.12 | Supply and fix; 930mm wide x 2100mmhigh overall palisade emergency-door comprising of robust vertical steel pales secured to horizonal rails, including all necessary iron mongery i.e hasps and staple and applying one coat red oxide primer before delivery to site and handing gate to posts (m.s.) | 1 | Nr |  | 0
4 | PAINTING
Prepare and apply to surfaces; spray three coats of gloss-oil-paint on;
4.1 | Palisade surfaces; internal and external | 19 | M2 |  | 0 | 18.9
4.2 | Gate surfaces; ditto; | 5 | M2 |  | 0 | 5.229
4.3 | Emergency-Door surfaces; ditto | 2 | M2 |  | 0 | 1.953
Prepare and apply; three-coats of weather-guard paints on;
4.4 | Plastered wall surfaces | 30 | M2 |  | 0
5 | POWER SUPPLY
5.1 | Electricity 3 Phase, supply and fix; armored cable (4mmx3core), about 15m in the ground from PSA-plant, 5m up to dB in the PSA-plant; including excavation and backfilling, UPVC-Class-B-100mmΦ for underground-cable; complete with dB, Industrial-Switch-Socket-Outlet, cables and all necessary accessories; | 1 | Item |  | 0
5.2 | Supply and fix; Security Lights-250W; complete with 50mmΦ steel-poles; complete with cables, photocell-switch and all necessary accessories; | 2 | Nr |  | 0
6 | WATER-NETWORK
6.1 | Supply and fix; appropriate 1-Water-tap; 32mm OD HDPE pipe, PE 100 PN 10 with all accessories and pipe-fittings for emergency water use when required like defrezing from the source which is about 118m away in the ground; | 1 | Item |  | 0
6.2 | Supply and install 1-in-No 100mm norminal diameter underground / pillar fire hydrant with two outlets of 65mm, type "ANGUS" or similar to be approved; Supply and lay fire hydrant pipes 100mm diameter 118m-long including excavating, backfilling, elbows, bends and any other associated accessories. (Minimum cover); Supply and install 2-in-No 100mm diameter stop valve for fire hydrant water supply main. | 1 | Item |  | 0
| SUB-TOTAL |  |  |  | 0
| VAT-18% |  |  |  | 0
| TOTAL |  |  |  | 0

## TRRH
BILLS OF QUANTITIES [BOQs]
CIVIL WORKS - RFP/CHAI-TZ-EPIC-CIVIL 001/25
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
PREAMBLES
A1 | The project will include six (6) main tasks namely; i) Reinforced concrete plinth to support the 6t-VIE-Tank; ii) Palisade fencing around three-sides of the plinth perimeter; iii) Solid-concrete-blocks wall on one side of the plinth perimeter and, Paving-blocks Apron around the plinth-perimeter; iv) Electrical installations that include 3-phase-power-socket and, 2-security-lights fixed on steel-poles; v) Tap-water near oxygen-tank for de-icing of valves or to handle emergency situations; vi) Fire-fighting-system (Hydrant-Outlet)
A2 | Engagement of Registered Building Contractor by Contractors Registration Board (CRB) is inavitable also, a specialist domestic Electrical Sub-contractor is necessary for appropriate sketch and implementation of power and security-lights
A3 | The VIE-Tank will be supplied and installed by other Vendor; but, she will also supply the Anchor-Bolts to be embedded in the reinforced concrete slab by you as per the Drawings; joint-consultation-and-coordination are required;
A4 | Anchor-Bolts for Vaporizers will be supplied and fixed in reinforced concrete slab complete with washers by you;
A5 | The Fire-fighting-system (Hydrant-Output) allowance is provisional subject to the outcome of the tender; as-built-sketches will be required before commissioning;
A6 | The Temeke Regional Referral Hospital (TRRH) is located at the right-rear-side of the hospital with no problem on allowance for setbacks; within TRRH in DAR ES SALAAM City;
PRELIMINARIES
B1 | By-Laws | 1 | Item |  | 0
B2 | Power for the works | 1 | Item |  | 0
B3 | Water for the works | 1 | Item |  | 0
B4 | Plants such as Concrete-Mixer, Plate-Compactor; Working-tools such as ladders; and the like; | 1 | Item |  | 0
B5 | Transport for materials | 1 | Item |  | 0
B6 | Construction management | 1 | Item |  | 0
B7 | Mix-Design for Reinforced Concrete Grade-30 | 1 | Item |  | 0
B8 | Testing of Materials (sand; aggregates; reinforcements; water) and Components (concrete-cubes; solid-blocks/bricks) | 1 | Item |  | 0
B9 | Cleaning the site for commissioning; | 1 | Item |  | 0
B10 | Signage | 1 | Item |  | 0
B11 | Safety-gears | 1 | Item |  | 0
B12 | UPVC-4" Pipe; for all services from the tank; | 1 | Item |  | 0
1 | DEMOLITIONS AND ALTERATIONS
1.1 | Presence of existing mango-tree for pruning and; dispose debris away from site; | 1 | Item |  | 0
2 | EXCAVATION AND EARTHWORK
Site preparation
2.1 | Excavate Oversite average 300mm deep to remove vegetable soil load up wheel and cart away | 60 | M2 |  | 0 |  |  | 7 | 7 | 4.49 | 2.5 | 60.225
General excavation
Trenches excavation
2.2 | Excavate to reduce levels not exceeding 1.5m deep from stripped level | 90 | M3 |  | 0 |  | 90.3375
Backfilling excavated materials
2.3 | Level and compact surface of excavation or filling in layers not exceeding 200mm thick | 77 | M3 |  | 0
Surplus excavated material
2.4 | load up and remove surplus excavated material to stockpile on/off site not exceeding 40km distance | 13 | M3 |  | 0 |  | 12.5 | 0.56025 | 13.0602 | 13.0602
Imported Sand; deposited and compacted in layers granular fill compacted in 150mm layers to 95% maximum dry density (m.d.d)
2.5 | Around foundations | 8 | M3 |  | 0 |  | 6 | 1.647 | 7.647
2.6 | On top of hardcore | 2 | M3 |  | 0 |  | 42.175 | 2.1088
Plunking and Strutting
2.7 | Allow for planking and strutting to sides of excavations | 1 | Item |  | 0
Disposal of Water
2.8 | Allow for keeping excavations free from mud and all water including spring and running water by pumbing pailing and other approved means | 1 | Item |  | 0
Blinding; Grade 10 (nominal mix 1:3:6; 15N/mm2 at 28 days)
2.9 | 50mm thick to receive hardcore bed (m.s.) | 42 | M2 |  | 0 |  | 42.175
Hardcore Bed
2.1 | 200mm thick layer approved hardcore filling well watered, rolled and compacted in layers not exceeding 150mm thick under floors to level and slope as required | 42 | M2 |  | 0
Soil Sterilization
2.11 | TERMIDOR 25EC' or other equal and approved chemical anti-termitr treatment to top surfaces of sand-blinded hardcore | 42 | M2 |  | 0
Damp Proof Membrane (DPM)
2.12 | 1000 gauge polythene damp-proof sheeting laid on blinded smooth finished hardcore bed with 300mm side and end laps to receive conrete bed (m.s) | 42 | M2 |  | 0
In-situ Reinforced Concrete; Raft-Foundation; Grade 30
2.13 | 500mm thick floor slab | 25 | M2 |  | 0 | 25
2.14 | 150mm thick Ramp; sloping not exceeding 45° from horizontal; | 5 | M2 |  | 0 | 4.707
2.15 | Ground beam | 2 | M3 |  | 0 | 2.3244
Reinforcement including bends, hooks, tying wires, distant blocks and ordinary spacers; Hot Rolled; High Yield Steel Bars BS 4449 - Assorted sizes as per the drawings; High Yield Strength 460MPa; Cutting and Bending as per BS 8666; to slabs and beams (Provisional)
2.16 | Y20 | 323 | Kg |  | 0
2.17 | Y16 | 323 | Kg |  | 0
2.18 | Y12 | 200 | Kg |  | 0
2.19 | Y10 | 11 | Kg |  | 0
2.2 | Assorted sizes (provisional) | 100 | Kg |  | 0
Sawn Formwork; vertical or battering surfaces
2.21 | Edges of ground-beams; 500mm girth | 32 | M |  | 0 | 20 |  | 5.49
2.22 | Ditto; 150mm girth | 6 | M |  | 0
Plinth Finishing
2.23 | 12mm thick cement sand mix (1:3) plastering; 3mm thick stucco or equal and approved surface well lied with steel trowelled finish on concrete surfaces | 11 | M2 |  | 0 | 10.8235
2.24 | Prepare and apply three coats of black bituminous paint to rendered surfaces of plinths | 11 | M2 |  | 0
Floor Finish
2.25 | 32mm thick cement sand mix (1:3) screed well lied with steel-trowelled finish; | 30 | M2 |  | 0
Holding Down Anchor Bolts
2.26 | Tank to be anchored down using HILTI-Chemical-Anchors (to be supplied and specified by tank manufacturer) to be appropriately embedded in the reinforced-concrete-slab; with minimum of 2-anchor-bolts in each-leg making 6-anchor-bolts; as per the drawings | 1 | Item |  | 0
2.27 | Supply and fix rectangular-hollow-sections; 75x75x2.5mm, 2400mm high, main members; including 300mm deep embedded in reinforced concrete slab; | 10 | Nr |  | 0
2.28 | Supply and fix Anchor-bolts complete with washels to receive Vaporiser (to be supplied and specified by manufacturer) | 1 | Item |  | 0
Foundation Apron around plinth-perimeter
2.29 | 600x600x50mm; Concrete-Paving-Slabs around | 11 | M2 |  | 0 | 12 | 1.494 | 10.506
3 | FENCING (SOLID BLOCKWORK AND PELISADE)
3.1 | 230mm thick Solid cement-sand blocks with strength of 4.5MPa: bedded and jointed in cement/sand mortar(1:4): external | 15 | M2 |  | 0 | 15.072 | 640
3.2 | Plastering internal; 12mm thick mix 1:3) cement sand plaster; 3mm thick stucco or equal and approved to masonry-walling | 30 | M2 |  | 0 | 15.072
3.3 | 230x400mm In-situ reinforced concrete Beam Grade-30 including necessary shuttering | 1 | M3 |  | 0 | 0.57776
Roofing (provisional)
3.4 | Supply and fabricate; welded and socketed; 50x50x4mm Mild-steel Angle Section Trusses and Purlins; apply two coats of anti-rust-paint and; one finishing gloss-oil-paint; | 32 | M |  | 0 | 15.708 | 914 | 3.656 | 19.364 | 12.4 | 31.764
3.5 | Supply gauge 26 gauge IT5 Resincoated Alu-zink roof sheets including self-drilling screws and fix to metal purlins. | 12 | M2 |  | 0 | 12.028
3.6 | Supply and fix gauge 26 resincoated plain-sheets welded to 375mm Barge; | 6 | M |  | 0 | 6.2
3.7 | Supply and fix gauge 26 resincoated plain-sheets welded to 100mm Fascia; | 6 | M |  | 0
3.8 | 300mm girth Metal Gutter 6m long complete with clips and one down-pipe 2.4 high; | 1 | Item |  | 0
Palisade Fence
3.9 | Supply and fix palisade fence; 2100mm high, robust vertical rectangular hollow sections 25x25x1.5mm, infill-materials; complete with 25x25x1.5mm 3-horizontal-bracings; | 9 | M |  | 0
3.1 | Supply and fix; 300mm high razor-wire with its tension-wire; on top of fence, gate and door; | 9 | M |  | 0 | 7800 | 0.93 | 2.28 | 10.08 | 9.15
Gate and Emergency Door
3.11 | Supply and fix; Double-Leafs; 2490mm wide x 2100mm high overall palisade gate comprising of robust vertical steel pales secured to horizonal rails, including all necessary iron mongery i.e hasps and staple and applying one coat red oxide primer before delivery to site and handing gate to posts (m.s.) | 1 | Nr |  | 0
3.12 | Supply and fix; 930mm wide x 2100mmhigh overall palisade emergency-door comprising of robust vertical steel pales secured to horizonal rails, including all necessary iron mongery i.e hasps and staple and applying one coat red oxide primer before delivery to site and handing gate to posts (m.s.) | 1 | Nr |  | 0
4 | PAINTING
Prepare and apply to surfaces; spray three coats of gloss-oil-paint on;
4.1 | Palisade surfaces; internal and external | 19 | M2 |  | 0 | 18.9
4.2 | Gate surfaces; ditto; | 5 | M2 |  | 0 | 5.229
4.3 | Emergency-Door surfaces; ditto | 2 | M2 |  | 0 | 1.953
Prepare and apply; three-coats of weather-guard paints on;
4.4 | Plastered wall surfaces | 30 | M2 |  | 0
5 | POWER SUPPLY
5.1 | Electricity 3 Phase, supply and fix; armored cable (4mmx3core), about 97m in the ground from PSA-plant, 5m up to dB; including excavation and backfilling, UPVC-Class-B-100mmΦ for underground-cable; complete with dB, Industrial-Switch-Socket-Outlet, cables and all necessary accessories; | 1 | Item |  | 0
5.2 | Supply and fix; Security Lights-250W; complete with 50mmΦ steel-poles; complete with cables, photocell-switch and all necessary accessories; | 2 | Nr |  | 0
6 | WATER-NETWORK
6.1 | Supply and fix; appropriate 1-Water-tap; 32mm OD HDPE pipe, PE 100 PN 10 with all accessories and pipe-fittings for emergency water use when required like defrezing from the source which is about 20m away in the ground; | 1 | Item |  | 0
6.2 | Supply and install 1-in-No 100mm norminal diameter underground / pillar fire hydrant with two outlets of 65mm, type "ANGUS" or similar to be approved; Supply and lay fire hydrant pipes 100mm diameter 20m-long including excavating, backfilling, elbows, bends and any other associated accessories. (Minimum cover); Supply and install 2-in-No 100mm diameter stop valve for fire hydrant water supply main. | 1 | Item |  | 0
| SUB-TOTAL |  |  |  | 0
| VAT-18% |  |  |  | 0
| TOTAL |  |  |  | 0