## PREAMBLES
ITEM | DESCRIPTION OF WORKS | QTY | UNIT | RATE | AMOUNT
PREAMBLES
1 | PROJECT NAME
Installations and Commission of Medical Gas Pipeline System (MGPS) at Abdulla Mzee Regional Hospital in Pemba and, Kivunge District Hospital in Unguja, Zanzibar
2 | DESCRIPTION
2.1 | The Clinton Health Access Initiative (CHAI), a sub-grantee of FHi360 under the EpiC project engages the services of a reputable and capable vendor to install Medical Gas Pipeline System (MGPS) including equipment, accessories and commission the same at Abdulla Mzee Regional Hospital - Pemba and Kivunge District Hospital - Unguja in Zanzibar as part of the efforts to improve medical Oxygen availability as per stated requirements
2.2 | The Bidder is expected to undertake the installations and commissioning only entailing that supply of all equipment / goods for installations will be provided, BUT all materials for welding plus the ones associated with civil-works, testing and commissioning are required;
3 | CLIENT
CHAI Program: Essential Medicine Program. Country: Tanzania Address: P.O Box 77277 Dar Es Salaam, Tanzania. Tel: +255-22-21219945
4 | PROJECT MANAGER
OHILIAB Consultancy Services, P.O. Box 3316, DAR ES SALAAM
5 | BIDDING DOCUMENTS
The preparation of the bid shall be read in conjunction with the following bidding documents: -
5.1 | Instructions to Bidders
5.2 | Purchase Order
5.2.1 | Recitals; [Reference, Description, Purchaser Information, Supplier Information, Contact Persons, Consignee Details, Applicable Incoterms, Delivery Locations, Delivery Date, Payment Schedules, Enclosures, Bills of Quantities (BOQs), Supplier Dossier (Technical Information; Proof of Quality; Warranties; Product Recall)]
5.2.2 | Terms and Conditions; Clause 1 to 30
5.2.3 | Annex-A; 1- Consignee details and required shipping documents
5.2.4 | Annex-B; 1- 1- Supply and installation requirement; 2-Specifications of automatic oxygen change over panel and pipeline system; 3-Flowmeter specification; 4-Humidifier Specification;
5.2.5 | Appendix 1: Abdulla Mzee Regional Hospital design drawings
5.2.6 | Appendix 2: Kivunge District Hospital design drawings
5.2.7 | Appendix 3: Matrix of Issues to be Negotiated
6 | HEALTH AND SAFETY
6.1 | Maintaining all safety equipment, personal protective equipment and any other assistance and equipment required to gain access to work areas | 1 | Item |  | 0
7 | COLLABORATIONS
7.1 | Ready to work with the equipment-supplier in case of equipment-weaknesses or defects | 1 | Item |  | 0
7.2 | Proper procedures for replacement of defective equipment or pipes | 1 | Item |  | 0
7.3 | Critical requirements/guidelines prior-to-installations | 1 | Item |  | 0
7.4 | Third-party inspections by Tanzania Medical and Drugs Authority (TMDA) or Zanzibar Medical and Drugs Authority (ZMDA) after installations on site are mandatory | 1 | Item |  | 0
7.5 | Conducting joint-user-trainings | 1 | Item |  | 0
0
8 | UNFORESEEN WORK BY CLIENT |  |  |  | 0
8.1 | The Bidder may state any unforeseen work substantiated with back-up-notes; | 1 | Sum |  | 0
0

## PIPELINES ABDULLAH
ITEM | DESCRIPTION OF WORKS | QTY | UNIT | RATE | AMOUNT
INSTALLATIONS ONLY
N | NOTES: -
N1 | THE INSTALLER IS REQUIRED TO ATTEND THE ENTIRE ELEMENT NR-01 - DEMOLITIONS AND ALTERATIONS AS DEFINED;
N2 | THE INSTALLER IS REQUIRED TO INSTALL ONLY ELEMENT NR-02; ALL EQUIPMENT, PIPES AND ACCESSORIES WILL BE PROVIDED BY ANOTHER SUPPLIER;
N3 | THE INSTALLER IS REQUIRED TO ALLOW SUM AMOUNT UNDER ELEMENT NR-03 FOR REPAIRING TO BE SPENT UPON APPROVALOF CHAI/A&E
The following assignment will only involve Installations and Commissioning only as the Equipment, Copper-pipes and Accessories such as elbows, reducers, couplers and tees will be provided;
Welding materials and welding are part of the assignment
1 | ELEMENT NR.- 01- DEMOLITIONS AND ALTERATIONS (PROVISIONAL)
1.1 | Cut and make holes to concrete or block walls; make good the surfaces by appropriate fillings and finishings; | 1 | Item |  | 0
1.2 | Create trench by excavation not exceeding 650x500mm deep; cast 50mm thick plain-concrete-blinding grade-10 on the footing; 100mm thick blockwork to trench wall-surcaces by cement sand mortar 1:4; 12mm thick cement sand 1:3 plastering to blockwork-surfaces-internal; fabricate removable top covers (precast-reinforced with BRC); approximately 10 meters long; | 1 | Item |  | 0
1.3 | Allow for introducing or repairing existing pipe-trunkings | 1 | Item |  | 0
2 | ELEMENT NR.- 02- MEDICAL GAS PIPELINES (PROVISIONAL)
FIXING MEDICAL GAS PIPELINE SYSTEM (MGPS) EQUIPMENT, INSTALLATION AND COMMISSIONING AT ABDULLAH MZEE REGIONAL HOSPITAL
MGPS Fittings or Units (to be provided)
2.1 | Medical gas terminal units | 64 | Nr |  | 0
2.2 | Oxygen flowmetre with humidifier | 64 | Nr |  | 0 | w-to-E
2.3 | Master alarm unit | 3 | Nr |  | 0
2.4 | Area Alarm unit | 4 | Nr |  | 0
2.5 | Zone Service Valves | 3 | Nr |  | 0
2.6 | Signal Cable | 1 | Item |  | 0
2.7 | Control board | 1 | Nr |  | 0
2.8 | Automatic Change-Over panel (Oxygen gas) | 1 | Nr |  | 0
Fixing supply-Degreased Copper Tubes (Pipes) and Accessories; screwed, welded and purged
In-trench Copper-pipe; clipped to trench-wall-surfaces from the VIE-Tank to Maternity-plinth-wall-elbow; (to be provided)
2.9 | 25mmØ X 0.9mm thick pipe | 11 | M |  | 0
2.1 | 25mmØ 90° elbows | 2 | Nr |  | 0
2.11 | 25mmØ straight couplers | 4 | Nr |  | 0
Free standing or clipped to surfaces; from Tee at maternity to upward through the wall; (to be provided)
2.12 | 25mmØ X 0.9mm thick pipe | 7 | M |  | 0
2.13 | 25mmØ 90° elbows | 1 | Nr |  | 0
2.14 | 25mmØ straight couplers | 3 | Nr |  | 0
2.15 | 25x15mmØ reducing couplings | 1 | Nr |  | 0
Free standing or clipped to surfaces; from Tee at maternity to pediatric/neonate-ward (at HDU corner) to; manifold; (to be provided)
2.16 | 15mmØ X 0.9mm thick pipe | 80 | M |  | 0
Extras - degressed copper fittings (to be provided)
2.17 | 15mmØ 90° elbows | 3 | Nr |  | 0
2.18 | 15mmØ straight couplers | 28 | Nr |  | 0
2.19 | 15x12mmØ reducing couplings | 5 | Nr |  | 0
2.2 | 15mmØ equal-tees | 3 | Nr |  | 0
2.21 | 15mmØ Lockable General/Line Valve | 1 | Nr |  | 0 | 251125
Clamps (to be provided)
2.22 | Brass munsen Rings – 25mmØ; | 9 | Nr |  | 0
2.23 | Brass munsen Rings – 15mmØ; | 40 | Nr |  | 0
Fixing distribution-Degreased Copper Tubes (Pipes) and Accessories; screwed, welded and purged
Free standing or clipped to surfaces; to all rooms in maternity-block and pediatric/neonate-ward and; in EMD (to be provided)
2.24 | 12mmØ X 0.7mm thick pipe | 209 | M |  | 0 | #REF!
Extras - degressed copper fittings (to be provided)
2.25 | 12mmØ 90° elbows | 24 | Nr |  | 0
2.26 | 12mmØ straight couplers | 72 | Nr |  | 0
2.27 | 12x10mmØ reducing couplings | 64 | Nr |  | 0
2.28 | 12mmØ equal-tees | 40 | Nr |  | 0
Free standing or clipped to surfaces; to all Points in maternity-block and pediatric/neonate-ward and; in EMD (to be provided)
2.29 | 10mmØ X 0.7mm thick pipe | 128 | M |  | 0
Extras - degressed copper fittings (to be provided)
2.3 | 10mmØ straight couplers | 44 | Nr |  | 0
Clamps (to be provided)
2.31 | Brass munsen Rings – 12mmØ; | 105 | Nr |  | 0
2.32 | Brass munsen Rings – 10mmØ; | 64 | Nr |  | 0
3 | ELEMENT - NR-03; REPAIR (IF ANY) AND CONNECT OLD PIPELINE OF EXISTING WARDS WITH NEW NETWORKS - ABDULLA MZEE HOSPITAL
3.1 | Allow for repairing and necessary interconnections | 1 | Sum |  | 0
| ABDULLAH MZEE - INSTALLATIONS OF MEDICAL PIPELINES CARRIED TO SUMMARY |  |  |  | 0

## PIPELINES KIVUNGE
ITEM | DESCRIPTION OF WORKS | QTY | UNIT | RATE | AMOUNT
INSTALLATIONS ONLY
N | NOTES: -
N1 | THE INSTALLER IS REQUIRED TO ATTEND THE ENTIRE ELEMENT NR-01 - DEMOLITIONS AND ALTERATIONS AS DEFINED;
N2 | THE INSTALLER IS REQUIRED TO INSTALL ONLY ELEMENT NR-02; ALL EQUIPMENT, PIPES AND ACCESSORIES WILL BE PROVIDED BY ANOTHER SUPPLIER;
N3 | THE INSTALLER IS REQUIRED TO ALLOW SUM AMOUNT UNDER ELEMENT NR-03 FOR REPAIRING TO BE SPENT UPON APPROVALOF CHAI/A&E
The following assignment will only involve Installations and Commissioning only as the Equipment, Copper-pipes and Accessories such as elbows, reducers, couplers and tees will be provided;
Welding materials and welding are part of the assignment
1 | ELEMENT NR.- 01- DEMOLITIONS AND ALTERATIONS (PROVISIONAL)
1.1 | Cut and make holes to concrete or block walls; make good the surfaces by appropriate fillings and finishings; | 1 | Item |  | 0
1.2 | Create trench by excavation not exceeding 650x500mm deep; cast 50mm thick plain-concrete-blinding grade-10 on the footing; 100mm thick blockwork to trench wall-surcaces by cement sand mortar 1:4; 12mm thick cement sand 1:3 plastering to blockwork-surfaces-internal; fabricate removable top covers (precast-reinforced with BRC); approximately 122 meters long; | 1 | Item |  | 0
1.3 | Allow for introducing or repairing existing pipe-trunkings | 1 | Item |  | 0
2 | ELEMENT NR.- 02- MEDICAL GAS PIPELINES (PROVISIONAL)
FIXING MEDICAL GAS PIPELINE SYSTEM (MGPS) EQUIPMENT, INSTALLATION AND COMMISSIONING AT KIVUNGE DISTRICT HOSPITAL - UNGUJA
MGPS Fittings or Units (to be provided)
2.1 | Medical gas terminal units | 30 | Nr |  | 0
2.2 | Oxygen flowmetre with humidifier | 30 | Nr |  | 0
2.3 | Master alarm unit | 3 | Nr |  | 0
2.4 | Area Alarm unit | 3 | Nr |  | 0
2.5 | Zone Service Valves | 3 | Nr |  | 0
2.6 | Signal Cable | 1 | Item |  | 0
2.7 | Control board | 1 | Nr |  | 0
2.8 | Automatic Change-Over panel (Oxygen gas) | 1 | Nr |  | 0
Fixing supply-Degreased Copper Tubes (Pipes) and Accessories; screwed, welded and purged
In-trench Copper-pipe; clipped to trench-wall-surfaces from the Tee at OPD/Admin junction to Maternity-plinth-wall-elbow; (to be provided)
2.9 | 25mmØ X 0.9mm thick pipe | 122 | M |  | 0
2.1 | 25mmØ 90° elbows | 4 | Nr |  | 0
2.11 | 25mmØ straight couplers | 42 | Nr |  | 0
2.12 | 25mm Ø equal-tees | 1 | Nr |  | 0
2.13 | 25x15mmØ reducing couplings | 2 | Nr |  | 0
From Tee entering Ground Floor (operating-room; recovery; postnatal; delivery-1&2; antenatal)
Free standing or clipped to surfaces (to be provided)
2.14 | 15mmØ X 0.9mm thick pipe | 37 | M |  | 0
Extras - degressed copper fittings (to be provided)
2.15 | 15mmØ 90° elbows | 1 | Nr |  | 0
2.16 | 15mmØ straight couplers | 13 | Nr |  | 0
2.17 | 15x12mmØ reducing couplings | 7 | Nr |  | 0
2.18 | 15mm Ø equal-tees | 6 | Nr |  | 0
2.19 | 15mmØ Lockable General/Line Valve | 2 | Nr |  | 0
Clamps (to be provided)
2.2 | Brass munsen Rings – 25mmØ; | 61 | Nr |  | 0
2.21 | Brass munsen Rings – 15mmØ; | 19 | Nr |  | 0
Fixing distribution-Degreased Copper Tubes (Pipes) and Accessories; screwed, welded and purged
Free standing or clipped to surfaces in the Maternity Ward Ground Floor-(operating-room; recovery; postnatal; delivery-1&2; antenatal); (to be provided)
2.22 | 12mmØ X 0.7mm thick pipe | 42 | M |  | 0
Extras - degressed copper fittings (to be provided)
2.23 | 12mmØ 90° elbows | 7 | Nr |  | 0
2.24 | 12mmØ straight couplers | 15 | Nr |  | 0
2.25 | 12mm Ø equal-tees | 3 | Nr |  | 0
Clamps (to be provided)
2.26 | Brass munsen Rings – 12mmØ; | 21 | Nr |  | 0
Fixing Degreased Copper Tubes (Pipes) and Accessories; screwed, welded and purged
From Tee entering First Floor-Pediatric ward (PICU; General-Neonate; Padeatric ward-1&2; NICU)
Free standing or clipped to surfaces (to be provided)
2.27 | 15mmØ X 0.9mm thick pipe | 48 | M |  | 0
Extras - degressed copper fittings (to be provided)
2.28 | 15mmØ 90° elbows | 5 | Nr |  | 0
2.29 | 15mmØ straight couplers | 17 | Nr |  | 0
2.3 | 15x12mmØ reducing couplings | 13 | Nr |  | 0
2.31 | 15mm Ø equal-tees | 5 | Nr |  | 0
2.32 | 15mmØ General/Line Valve | 2 | Nr |  | 0
Clamps (to be provided)
2.33 | Brass munsen Rings – 15mmØ; | 24 | Nr |  | 0
Fixing distribution-Degreased Copper Tubes (Pipes) and Accessories; screwed, welded and purged
Free standing or clipped to surfaces in the First Floor-Pediatric ward (PICU; General-Neonate; Padeatric ward-1&2; NICU) (to be provided)
2.34 | 12mmØ X 0.7mm thick pipe | 45 | M |  | 0
Extras - degressed copper fittings (to be provided)
2.35 | 12mmØ 90° elbows | 3 | Nr |  | 0
2.36 | 12mmØ straight couplers | 16 | Nr |  | 0
2.37 | 12mm Ø equal-tees | 5 | Nr |  | 0
Clamps (to be provided)
2.38 | Brass munsen Rings – 12mmØ; | 23 | Nr |  | 0
Fixing supply-Degreased Copper Tubes (Pipes) and Accessories; screwed, welded and purged
From Tee entering Second Floor-HDU
Free standing or clipped to surfaces (to be provided)
2.39 | 15mmØ X 0.9mm thick pipe | 20 | M |  | 0
Extras - degressed copper fittings (to be provided)
2.4 | 15mmØ 90° elbows | 3 | Nr |  | 0
2.41 | 15mmØ straight couplers | 7 | Nr |  | 0
2.42 | 15x12mmØ reducing couplings | 6 | Nr |  | 0
2.43 | 15mm Ø equal-tees | 5 | Nr |  | 0
2.44 | 15mmØ General/Line Valve | 1 | Nr |  | 0
Clamps (to be provided)
2.45 | Brass munsen Rings – 15mmØ; | 10 | Nr |  | 0
Fixing distribution-Degreased Copper Tubes (Pipes) and Accessories; screwed, welded and purged
Free standing or clipped to surfaces in the Second Floor-HDU; (to be provided)
2.46 | 12mmØ X 0.7mm thick pipe | 10 | M |  | 0
Extras - degressed copper fittings; (to be provided)
2.47 | 12mmØ straight couplers | 4 | Nr |  | 0
Clamps (to be provided)
2.48 | Brass munsen Rings – 12mmØ; | 5 | Nr |  | 0
Free standing or clipped to surfaces; to all Points in maternity-block and pediatric/neonate-ward and; (to be provided)
2.49 | 10mmØ X 0.7mm thick pipe | 60 | M |  | 0
Extras - degressed copper fittings (to be provided)
2.5 | 10mmØ straight couplers | 21 | Nr |  | 0
Clamps (to be provided)
2.51 | Brass munsen Rings – 10mmØ; | 30 | Nr |  | 0
3 | ELEMENT NR - 03; REPAIR (IF ANY) AND CONNECT OLD PIPELINE OF EXISTING WARDS WITH NEW NETWORKS - KIVUNGE DH
3.1 | Allow for repairing and necessary interconnections | 1 | Sum |  | 0
| KIVUNGE - INSTALLATIONS OF MEDICAL PIPELINES CARRIED TO SUMMARY |  |  |  | 0

## SUMMARY
ITEM | DESCRIPTION |  | PAGE | TOTAL TSHS
INSTALLATIONS & COMMISSIONING OF PIPELINES SYSTEM (MGPS) - ZANZIBAR
SUMMARY
A | ABDULLAH MZEE REGIONAL HOSPITAL - PEMBA |  |  | 0
B | KIVUNGE DISTRICT HOSPITAL - UNGUJA |  |  | 0
C | PREAMBLES |  |  | 0
|  | SUB-TOTAL |  | 0
|  | ADD; VAT 18% |  | 0
| MEDICAL GAS PIPELINES - ZANZIBAR |  |  | 0