## Ethiopia (hidden)
Cylinders
Product | Category | Specifications | Meets specifications? | Notes
Cylinders | DESCRIPTION | A container designed as a refillable cylinder used to hold compressed medical oxygen (O2) under safe conditions at high pressure (e.g. 50–200 bar). It is typically filled with oxygen when delivered from the gas supplier and includes a valve stem, an opening/closing valve, and will be graded according to size (capacity) and colour-coded to denote oxygen content. The cylinder may be made of steel, aluminium (Al) or other ferrous or non-ferrous materials and must be used together with a pressure regulator in order to release the oxygen at the correct working pressure. (SOURCE: GMDN 47225)
| Technical | Refillable cylinders for compressed oxygen gas for medical use.
Sizes: "J" - 47.2 L water (6,800 L @ 137 bar)
Nominal / working pressure: 137-150 bar
Neck thread 25E or equivalent
Valve stem as per standards, Bullnose BS 341 valve outlet
Valve assembly material: brass
Valve handle operated, supplied with tools.
Material: CGA approved seamless steel/aluminum alloy/carbon fibre/other composite body
Colour coding: according to ISO/ANSI/CGA/NFPA
Supplied with valve stem cap & safety cap
Stamped onto shoulder:
· Nominal and test pressures
· Cylinder capacity (water litres)
· Weight (kg)
· Date of manufacture
· Serial number
· Company and country of origin
· transport rating (UN stamp)
· inspection agency stamp and "p" marking
Environmental:
· Suitable for continuous operation in ambient temperature of at least 5–45 °C, relative humidity of at least 15–90% non condensing
· Capable of being stored in ambient temperature of at least 5–50 °C, relative humidity of at least 15–95% non condensing
| Warranty | 5 years recommended
| QMS | ISO 9001 (General QMS)
| Regulatory | CE indicated by pi, "p" (Cylinders fall under TPED)
| Product performance standards | ISO 10297: Gas cylinders – Cylinder valves – Specification and type testing
| Where testing indicated, must be done by an accredited laboratory | ISO 14246: Gas cylinders – Cylinder valves – Manufacturing tests and examinations
ISO 9809-1: Gas cylinders – Refillable seamless steel gas cylinders – Design, construction and testing
ISO 13769: Gas cylinders — Stamp marking
ISO 13341: Gas cylinders – Fitting of valves to gas cylinders
ISO 15996: Gas cylinders – Residual pressure valves – Specification and type testing of cylinder valves incorporating residual pressure devices
ISO 11363-1: Gas cylinders — 17E and 25E taper threads for connection of valves to gas cylinders
ISO 15001: Anaesthetic and respiratory equipment – Compatibility with oxygen
| Regional/local standards | Country-specific and regional colour gas coding and other standards apply and must be listed.
| Packaging | Name and/or trade mark and address of the manufacturer.
Product name.
Product reference.
Type of product and main characteristics.
Performance testing information against the mentioned standards.
Lot number prefixed by the word "LOT" (or equivalent harmonised symbol).
Expiry date by year and month, prefixed by the word "EXP" (or equivalent harmonised symbol).
Information for particular storage conditions (temperature, pressure, light, humidity, etc.), as appropriate (or equivalent harmonised symbol), if applicable.
Information for handling, if applicable (or equivalent harmonised symbol).
If the packaging is not transparent, it must bear a diagram (preferably actual size) showing the essential parts of the product and indicating the position of the product in the packaging.
Gross Weight.
Cubic Measurement.
All indicated at least in English.
Regulator with Manometer
Product | Category | Specifications | Meets specifications? | Notes
Pressure regulator | Description | A reduction valve designed to be attached through a gas-tight connector (e.g., a pin-index or bull-nosed screw thread connection) to the valve stem of an oxygen (O2) cylinder to lower high, variable gas pressure (e.g., 50–250 bar) to a lower, constant working pressure, typically 3–5 bar. It can be a single- or a dual-stage regulator, usually of a piston or diaphragm design. It will have a safety relief valve to avoid excessive pressure due to increased ambient temperatures, and it may have associated devices, usually a manometer or manometers, to display the available gas reserve of a gas cylinder and the working pressure. (SOURCE: GMDN 43438)
High-pressure gas regulators are placed between the output port of the high-pressure gas container at one end and the patient breathing circuit at the other end.
| Technical | Pressure regulator assembly to have inlet connections compatible with the following valve(s) (indicated in addendum table):
·Bullnose
Outlet connection: standard DISS, male
Steel/plated brass/aluminium casing, brass valve.
Nominal inlet pressure 13 700 kPa (137 bar, 1987 psi), maximum 20 000 kPa (200 bar, 2901 psi).
Outlet pressure 345 kPa (3.5 bar, 50 psi).
Integrated manometer, 0–20 000 kPa (0–200 bar, 0–2901 psi).
Safety over-pressure release valve.
Pressure regulator supplied with flowmeter, if required (see specifications)
Rated for use with medical oxygen (clearly indicated on manometer)
| Warranty | 2 years minimum
| After sales | Availability of repair and/or service level agreements
| Standards | ISO 13485 (medical device QMS)
ISO 14971 (application of risk management)
| Regulatory | CE and/or
FDA-registered
| Product performance standards | ISO 10524 Pressure regulators for use with medical gases.
ISO 15001 Anaesthetic and respiratory equipment – Compatibility with oxygen.
ISO 15223-1 Medical devices – Symbols to be used with medical device labels, labelling and information to be supplied – Part 1: General requirements.
| Packaging | Name and/or trademark and address of the manufacturer.
Product name.
Product reference.
Type of product and main characteristics.
Performance testing information against the mentioned standards.
Lot number prefixed by the word "LOT" (or equivalent harmonised symbol).
Information for particular storage conditions (temperature, pressure, light, humidity, etc.), as appropriate (or equivalent harmonised symbol), if applicable.
Information for handling, if applicable (or equivalent harmonised symbol).
If the packaging is not transparent, it must bear a diagram (preferably actual size) showing the essential parts of the product and indicating the position of the product in the packaging.
Gross Weight.
Cubic Measurement.
All indicated at least in English.
Flowmeter
Product | Category | Specifications | Meets specifications? | Notes
Flowmeter, Thorpe tube, pressure compensated | Description | A device intended to measure and regulate the flow of a medical gas [e.g., oxygen (O2), carbon dioxide (CO2), nitrous oxide (N2O), helium/oxygen gas mixture (heliox), medical air] during various procedures (e.g., therapeutic administration, anesthesia, insufflation during surgery). It consists of an upright tube containing a float, which rises and falls in relation to gas flow, and a distal valve (compensated flowmeter) to control gas flow rate. It will be calibrated to a specific medical gas and have a dedicated flow rate range; therefore, some types may be dedicated to a specific patient group (e.g., neonate, infant, adult) or clinical use. (SOURCE: GMDN)
Oxygen respiration flowmeters are intended for use with a variety of oxygen-supply systems such as central piped systems, cylinders valves, or concentrators and are connected to various delivery modalities or interfaces such as to a patient circuit or a medical device that uses or delivers the gas, including nasal cannulae or various types of mask-patient interfaces.
| Technical | Device suitable for use with medical oxygen
Thorpe tube flowmeter type, contains inlet and outlet port, a flow regulator, a valve and a clear measuring tube
Flowmeters to measure and regulate flow from an already pressure-reduced and regulated oxygen source to the patient or other medical device
Pressure compensated flowmeters, calibrated at 345–380 kPa (3.4–3.8 bar, 50–55 psi) inlet gauge pressure.
Max gauge inlet pressure 690 kPa (6.9 bar, 100 psi).
Flow adjustment knobs to have rough surface to prevent slipping.
Flowmeters calibrated to the following flow range, all metric (indicated in addendum table):
0-15 L/min, accuracy 10%, dual taper graduations 0.5 L/min (0–5 L/min range) and 1 L/min (5 L/min – maximum range)
0-70 L/min, accuracy 10%, single taper graduations 5 L/min full range
All minimum flowrates to be zero when fully closed
All graduations to be clearly visible for 270 degrees (most breadth for provider vantage points)
Inlet and outlet ports to be clearly specified and will in part be determined by use case (suitable for connection to centralized system, cylinders, concentrators or compressors) (indicated in addendum table):
Cylinder source inlet: Connection to a pressure regulator
Confirm inlet connection of flowmeter to be DISS, female (specify otherwise)
Outlets:
Specify outlet adapter, e.g., "Christmas tree" tubing adapter, DISS female to barbed 1/4 inch ID (male) hose connector or DISS, male (indicated in addendum table)
Flowmeter material:
Column to be transparent, clear, shatter-resistant, medical-grade polymer (polypropylene, polycarbonate)
Hardware/valves: Brass/steel/aluminum
All materials in contact with oxygen certified for medical use.
Internal parts (e.g., valve, inlet filter if present), replaceable by user.
Environmental
Capable of being stored in ambient temperature of at least 5–50 °C, relative humidity of at least 15–95% non-condensing.
Suitable for continuous operation in ambient temperature of at least 5–45 °C, relative humidity of at least 15–90% non-condensing.
Specific requirements for altitude may be required, depending on the installation site.
Disinfectable with hospital grade detergents.
| Warranty | 2 years minimum
| After sales | Availability of repair and/or service level agreements
| Regulatory | CE and/or
FDA-registered
| Product performance standards | ISO 32 Gas cylinders for medical use — Marking for identification of content (or ANSI equivalent)
ISO 5359 Low-pressure hose assemblies for use with medical gases.
ISO 15001 Anesthetic and respiratory equipment – Compatibility with oxygen.
ISO 15223-1 Medical devices – Symbols to be used with medical device labels, labelling and information to be supplied – Part 1: General requirements.
ISO 18082 Anesthetic and respiratory equipment – Dimensions of non-interchangeable screw-threaded (NIST) low-pressure connectors for medical gases.
ISO 18562 Biocompatibility evaluation of breathing gas pathways in healthcare applications.
| Packaging | Name and/or trade mark and address of the manufacturer.
Product name.
Product reference.
Type of product and main characteristics.
Performance testing information against the mentioned standards.
Lot number prefixed by the word "LOT" (or equivalent harmonized symbol).
Information for particular storage conditions (temperature, pressure, light, humidity, etc.), as appropriate (or equivalent harmonized symbol), if applicable.
Information for handling, if applicable (or equivalent harmonized symbol).
If the packaging is not transparent, it must bear a diagram (preferably actual size) showing the essential parts of the product and indicating the position of the product in the packaging.
Gross Weight.
Cubic Measurement.
All indicated at least in English.
Humidifier
Product | Category | Specifications | Meets specifications? | Notes
Bubble Humidifier | Description | A device designed to prevent the drying of airway passages associated with the inhalation of oxygen (O2) by adding water vapor to the dry gas as it is passed through, or more seldom, over water. It typically consists of a graduated container (reservoir) for the water, a top piece that functions as a detachable lid (typically a screw lid with a gastight seal), and a tube that protrudes into the water to divert the gas below the water level. This device, commonly known as a bubble humidifier, does not heat the water. It has connectors: 1) one (e.g., a winged nut) that connects to an oxygen therapy flowmeter; and 2) one to which the patient tubing is connected. This is a reusable device. (SOURCE: GMDN 35113)
| Technical | Reusable humidifier for oxygen therapy and ventilation/anesthesia inspiratory lines.
Non-heated humidifier - ambient temperature functionality.
Bubble-through humidification system.
Unbreakable or shatter resistant.
Transparent humidification bottle
Graduated, graduation shall show minimum and maximum water level.
Humidification chamber working volume at least 150 mL, not greater than 500 mL.
Detachable metal or rigid durable polymer cap with gas connectors.
Pressure relief safety valve, ≥ 14 kPa (0.1 bar, 2 psi) pressure rating.
DISS, female (nut) connectors for inlet.
6 mm barbed connector for outlet.
Flow rate capacity up to 15 L/min.
Must be capable of disinfection.
Materials, all to be certified for medical use:
Cap and connectors made of brass/steel/other biocompatible metal or polymer
Bottle and tubes made of polypropylene, polycarbonate or equivalent biocompatible plastic/polymer
Pressure valve made of brass chromium plated or equivalent metal
Supplier must define decontamination procedure.
| Warranty | 2 years minimum
| After sales | Availability of repair and/or service level agreements
| Standards | ISO 13485 (medical device QMS)
ISO 18562-1: Biocompatibility evaluation of breathing gas pathways in healthcare applications – Part 1: Evaluation and testing within a risk management process.
| Regulatory | CE and/or
FDA
| Product performance standards | ISO 15001 Anesthetic and respiratory equipment – Compatibility with oxygen.
ISO 15223-1 Medical devices – Symbols to be used with medical device labels, labelling and information to be supplied – Part 1: General requirements.
ISO 18562 Biocompatibility evaluation of breathing gas pathways in healthcare applications.
ISO 18562-1 Biocompatibility evaluation of breathing gas pathways in healthcare applications – Part 1: Evaluation and testing within a risk management process.
| Packaging | Name and/or trade mark and address of the manufacturer.
Product name.
Product reference.
Type of product and main characteristics.
Performance testing information against the mentioned standards.
Lot number prefixed by the word "LOT" (or equivalent harmonized symbol).
Expiry date by year and month, prefixed by the word "EXP" (or equivalent harmonized symbol).
Information for particular storage conditions (temperature, pressure, light, humidity, etc.), as appropriate (or equivalent harmonized symbol), if applicable.
Information for handling, if applicable (or equivalent harmonized symbol).
If the packaging is not transparent, it must bear a diagram (preferably actual size) showing the essential parts of the product and indicating the position of the product in the packaging.
Gross Weight.
Cubic Measurement.
All indicated at least in English.
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I've separated out the items in this tab to individual sheets, using same format as specs for other countries. Please see next tabs

## Cylinders
Vendor
Model
Product | Category | CHAI Specifications | Meet requirement? (Y/N) | Type of supporting documents (select from dropdown) | Page no. in supporting documents | Comments
Cylinders | DESCRIPTION | A container designed as a refillable cylinder used to hold compressed medical oxygen (O2) under safe conditions at high pressure (e.g. 50–200 bar). It is typically filled with oxygen when delivered from the gas supplier and includes a valve stem, an opening/closing valve, and will be graded according to size (capacity) and colour-coded to denote oxygen content. The cylinder may be made of steel, aluminium (Al) or other ferrous or non-ferrous materials and must be used together with a pressure regulator in order to release the oxygen at the correct working pressure. (SOURCE: GMDN 47225)
| Technical | Refillable cylinders for compressed oxygen gas for medical use.
"J" size - 47.2 L water (6,800 L @ 137 bar)
Nominal / working pressure: 137-150 bar
Primary valve:
· bullnose (BS 341 No.3 valve) - Ethiopia & Mozambique
· bullnose (NF E29-650/F ) - Cameroon
Valve assembly material: brass
Valve handle/key operated, supplied with tools.
Material: seamless steel/aluminum alloy/carbon fibre/other composite body
Colour coding: according to ISO 32 (Black body with white shoulders)
Valve protection:
· Valve cap - Ethiopia
· Valve guard - Mozambique & Cameroon
Stamped onto shoulder:
· Nominal and test pressures
· Cylinder capacity (water litres)
· Weight (kg)
· Date of manufacture
· Serial number
· Company and country of origin
· transport rating (DOT3AA or UN stamp)
· inspection agency stamp
Environmental:
· Suitable for continuous operation in ambient temperature of at least 5–45 °C, relative humidity of at least 15–90% non condensing
· Capable of being stored in ambient temperature of at least 5–50 °C, relative humidity of at least 15–95% non condensing
| Warranty | 5 years recommended
| QMS | ISO 9001 (General QMS)
| Regulatory | CE indicated by pi, "p" (Cylinders fall under TPED)
| Product performance standards Where testing indicated, must be done by an accredited laboratory - documentation of which to be included prior to shipment | ISO 10297: Gas cylinders – Cylinder valves – Specification and type testing
ISO 14246: Gas cylinders – Cylinder valves – Manufacturing tests and examinations
ISO 7866: Gas cylinders – Refillable seamless aluminium alloy gas cylinders – Design, construction and testing
ISO 9809-1: Gas cylinders – Refillable seamless steel gas cylinders – Design, construction and testing
ISO 13769: Gas cylinders — Stamp marking
ISO 13341: Gas cylinders – Fitting of valves to gas cylinders
ISO 15996: Gas cylinders – Residual pressure valves – Specification and type testing of cylinder valves incorporating residual pressure devices
ISO 11363-1: Gas cylinders — 17E and 25E taper threads for connection of valves to gas cylinders
ISO 15001: Anaesthetic and respiratory equipment – Compatibility with oxygen
| Regional/local standards | Country-specific and regional colour gas coding and other standards apply and must be listed.
| Packaging | Name and/or trade mark and address of the manufacturer.
Product name.
Product reference.
Type of product and main characteristics.
Performance testing information against the mentioned standards.
Lot number prefixed by the word "LOT" (or equivalent harmonised symbol).
Expiry date by year and month, prefixed by the word "EXP" (or equivalent harmonised symbol).
Information for particular storage conditions (temperature, pressure, light, humidity, etc.), as appropriate (or equivalent harmonised symbol), if applicable.
Information for handling, if applicable (or equivalent harmonised symbol).
If the packaging is not transparent, it must bear a diagram (preferably actual size) showing the essential parts of the product and indicating the position of the product in the packaging.
Gross Weight.
Cubic Measurement.
All indicated at least in English.
Extra information required: number of units.

## Pressure regulator, cylinder
Vendor
Model
Product | Spec category | Specs, WHO-UNICEF derived | Meet requirement? (Y/N) | Type of supporting documents (select from dropdown) | Page no. in supporting documents | Comments
Pressure regulator | DESCRIPTION | A reduction valve designed to be attached through a gas-tight connector (e.g. a pin-index or bull-nosed screw thread connection) to the valve stem of an oxygen (O2) cylinder to lower high, variable gas pressure (e.g. 50–250 bar) to a lower, constant working pressure, typically 3–5 bar. It can be a single- or a dual-stage regulator, usually of a piston or diaphragm design. It will have a safety relief valve to avoid excessive pressure due to increased ambient temperatures, and it may have associated devices, usually a manometer or manometers, to display the available gas reserve of a gas cylinder and the working pressure. (SOURCE: GMDN 43438) High-pressure gas regulators are placed between the output port of the high-pressure gas container at one end and the patient breathing circuit at the other end.
| Technical | Pressure regulator inlet connection:
· compatible with bullnose valve BS 341 (Oxygen) - Ethiopia & Mozambique
· complatible with bullnose NF E29-650/F (Oxygen) - Cameroon
Outlet connection standard DISS, male
Steel/plated brass/aluminium casing, brass valve.
Nominal inlet pressure 13 700 kPa (137 bar, 1987 psi), maximum 20 000 kPa (200 bar, 2901 psi).
Outlet pressure 345 kPa (3.5 bar, 50 psi).
Integrated manometer, 0–20 000 kPa (0–200 bar, 0–2901 psi).
Safety over-pressure release valve.
Rated for use with medical oxygen (clearly indicated on manometer)
| Warranty | Min. 1 year (ideal 2)
| Standards | ISO 13485 (medical device QMS)
ISO 14971 (application of risk management)
| Regulatory | CE
FDA
| Product performance standards | ISO 10524 Pressure regulators for use with medical gases.
ISO 15001 Anaesthetic and respiratory equipment – Compatibility with oxygen.
ISO 15223-1 Medical devices – Symbols to be used with medical device labels, labelling and information to be supplied – Part 1: General requirements.
| Packaging | Name and/or trade mark and address of the manufacturer.
Product name.
Product reference.
Type of product and main characteristics.
Performance testing information against the mentioned standards.
Lot number prefixed by the word "LOT" (or equivalent harmonised symbol).
Information for particular storage conditions (temperature, pressure, light, humidity, etc.), as appropriate (or equivalent harmonised symbol), if applicable.
Information for handling, if applicable (or equivalent harmonised symbol).
If the packaging is not transparent, it must bear a diagram (preferably actual size) showing the essential parts of the product and indicating the position of the product in the packaging.
Gross Weight.
Cubic Measurement.
All indicated at least in English.

## Cylinders, CMR (hidden)
Vendor
Model
Product | Category | CHAI Specifications | Meet requirement? (Y/N) | Type of supporting documents (select from dropdown) | Page no. in supporting documents | Comments
Cylinders | DESCRIPTION | A container designed as a refillable cylinder used to hold compressed medical oxygen (O2) under safe conditions at high pressure (e.g. 50–200 bar). It is typically filled with oxygen when delivered from the gas supplier and includes a valve stem, an opening/closing valve, and will be graded according to size (capacity) and colour-coded to denote oxygen content. The cylinder may be made of steel, aluminium (Al) or other ferrous or non-ferrous materials and must be used together with a pressure regulator in order to release the oxygen at the correct working pressure. (SOURCE: GMDN 47225)
| Technical | Refillable cylinders for compressed oxygen gas for medical use.
Size: 50L water capacity
Nominal / working pressure: 137-150 bar
Primary valve: Bullnose (NF E29-650/F )
Valve assembly material: brass
Valve handle/key operated, supplied with tools.
Material: CGA approved seamless steel/aluminum alloy/carbon fibre/other composite body
Colour coding: according to ISO 32 (Black body with white shoulders)
Supplied with valve guard
Stamped onto shoulder:
· Nominal and test pressures
· Cylinder capacity (water litres)
· Weight (kg)
· Date of manufacture
· Serial number
· Company and country of origin
· transport rating (DOT3AA or UN stamp)
· inspection agency stamp aligning with the regulatory approval
Environmental:
· Suitable for continuous operation in ambient temperature of at least 5–45 °C, relative humidity of at least 15–90% non condensing
· Capable of being stored in ambient temperature of at least 5–50 °C, relative humidity of at least 15–95% non condensing
| Warranty | 5 years recommended
| QMS | ISO 9001 (General QMS)
| Regulatory | CE indicated by pi, "p" (Cylinders fall under TPED) or US DOT
· applies to BOTH cylinders and valves
| Product performance standards Where testing indicated, must be done by an accredited laboratory - documentation of which to be included prior to shipment | ISO 10297: Gas cylinders – Cylinder valves – Specification and type testing
ISO 14246: Gas cylinders – Cylinder valves – Manufacturing tests and examinations
ISO 7866: Gas cylinders – Refillable seamless aluminium alloy gas cylinders – Design, construction and testing
ISO 9809-1: Gas cylinders – Refillable seamless steel gas cylinders – Design, construction and testing
ISO 13769: Gas cylinders — Stamp marking
ISO 13341: Gas cylinders – Fitting of valves to gas cylinders
ISO 15996: Gas cylinders – Residual pressure valves – Specification and type testing of cylinder valves incorporating residual pressure devices
ISO 11363-1: Gas cylinders — 17E and 25E taper threads for connection of valves to gas cylinders
ISO 15001: Anaesthetic and respiratory equipment – Compatibility with oxygen
| Regional/local standards | Country-specific and regional colour gas coding and other standards apply and must be listed.
| Packaging | Name and/or trade mark and address of the manufacturer.
Product name.
Product reference.
Type of product and main characteristics.
Performance testing information against the mentioned standards.
Lot number prefixed by the word "LOT" (or equivalent harmonised symbol).
Expiry date by year and month, prefixed by the word "EXP" (or equivalent harmonised symbol).
Information for particular storage conditions (temperature, pressure, light, humidity, etc.), as appropriate (or equivalent harmonised symbol), if applicable.
Information for handling, if applicable (or equivalent harmonised symbol).
If the packaging is not transparent, it must bear a diagram (preferably actual size) showing the essential parts of the product and indicating the position of the product in the packaging.
Gross Weight.
Cubic Measurement.
All indicated at least in English.
Extra information required: number of units.

## Cylinder pressure regulator CMR (hidden)
Vendor
Model
Product | Spec category | Specs, WHO-UNICEF derived | Meet requirement? (Y/N) | Type of supporting documents (select from dropdown) | Page no. in supporting documents | Comments
Pressure regulator | DESCRIPTION | A reduction valve designed to be attached through a gas-tight connector (e.g. a pin-index or bull-nosed screw thread connection) to the valve stem of an oxygen (O2) cylinder to lower high, variable gas pressure (e.g. 50–250 bar) to a lower, constant working pressure, typically 3–5 bar. It can be a single- or a dual-stage regulator, usually of a piston or diaphragm design. It will have a safety relief valve to avoid excessive pressure due to increased ambient temperatures, and it may have associated devices, usually a manometer or manometers, to display the available gas reserve of a gas cylinder and the working pressure. (SOURCE: GMDN 43438) High-pressure gas regulators are placed between the output port of the high-pressure gas container at one end and the patient breathing circuit at the other end.
| Technical | Pressure regulator inlet connection: Compatible with cylinder bullnose valves NF E29-650/F (Oxygen)
Outlet connection standard DISS, male
Steel/plated brass/aluminium casing, brass valve.
Nominal inlet pressure 13 700 kPa (137 bar, 1987 psi), maximum 20 000 kPa (200 bar, 2901 psi).
Outlet pressure 345 kPa (3.5 bar, 50 psi).
Integrated manometer, 0–20 000 kPa (0–200 bar, 0–2901 psi).
Safety over-pressure release valve.
Rated for use with medical oxygen (clearly indicated on manometer)
| Warranty | Min. 1 year (ideal 2)
| Standards | ISO 13485 (medical device QMS)
ISO 14971 (application of risk management)
| Regulatory | CE
FDA
| Product performance standards | ISO 10524 Pressure regulators for use with medical gases.
ISO 15001 Anaesthetic and respiratory equipment – Compatibility with oxygen.
ISO 15223-1 Medical devices – Symbols to be used with medical device labels, labelling and information to be supplied – Part 1: General requirements.
| Packaging | Name and/or trade mark and address of the manufacturer.
Product name.
Product reference.
Type of product and main characteristics.
Performance testing information against the mentioned standards.
Lot number prefixed by the word "LOT" (or equivalent harmonised symbol).
Information for particular storage conditions (temperature, pressure, light, humidity, etc.), as appropriate (or equivalent harmonised symbol), if applicable.
Information for handling, if applicable (or equivalent harmonised symbol).
If the packaging is not transparent, it must bear a diagram (preferably actual size) showing the essential parts of the product and indicating the position of the product in the packaging.
Gross Weight.
Cubic Measurement.
All indicated at least in English.

## Cylinders, MOZ (hidden)
Vendor
Model
Product | Category | CHAI Specifications | Meet requirement? (Y/N) | Type of supporting documents (select from dropdown) | Page no. in supporting documents | Comments
Cylinders | DESCRIPTION | A container designed as a refillable cylinder used to hold compressed medical oxygen (O2) under safe conditions at high pressure (e.g. 50–200 bar). It is typically filled with oxygen when delivered from the gas supplier and includes a valve stem, an opening/closing valve, and will be graded according to size (capacity) and colour-coded to denote oxygen content. The cylinder may be made of steel, aluminium (Al) or other ferrous or non-ferrous materials and must be used together with a pressure regulator in order to release the oxygen at the correct working pressure. (SOURCE: GMDN 47225)
| Technical | Refillable cylinders for compressed oxygen gas for medical use.
"J" size - 47.2 L water (6,800 L @ 137 bar)
Nominal / working pressure: 137-150 bar
Primary valve: bullnose (BS 341 No.3 valve)
Valve assembly material: brass
Valve handle/key operated, supplied with tools.
Material: CGA approved seamless steel/aluminum alloy/carbon fibre/other composite body
Colour coding: according to ISO 32 (Black body with white shoulders)
Supplied with valve guard
Stamped onto shoulder:
· Nominal and test pressures
· Cylinder capacity (water litres)
· Weight (kg)
· Date of manufacture
· Serial number
· Company and country of origin
· transport rating (DOT3AA or UN stamp)
· inspection agency stamp
Environmental:
· Suitable for continuous operation in ambient temperature of at least 5–45 °C, relative humidity of at least 15–90% non condensing
· Capable of being stored in ambient temperature of at least 5–50 °C, relative humidity of at least 15–95% non condensing
| Warranty | 5 years recommended
| QMS | ISO 9001 (General QMS)
| Regulatory | CE indicated by pi, "p" (Cylinders fall under TPED)
| Product performance standards Where testing indicated, must be done by an accredited laboratory - documentation of which to be included prior to shipment | ISO 10297: Gas cylinders – Cylinder valves – Specification and type testing
ISO 14246: Gas cylinders – Cylinder valves – Manufacturing tests and examinations
ISO 7866: Gas cylinders – Refillable seamless aluminium alloy gas cylinders – Design, construction and testing
ISO 9809-1: Gas cylinders – Refillable seamless steel gas cylinders – Design, construction and testing
ISO 13769: Gas cylinders — Stamp marking
ISO 13341: Gas cylinders – Fitting of valves to gas cylinders
ISO 15996: Gas cylinders – Residual pressure valves – Specification and type testing of cylinder valves incorporating residual pressure devices
ISO 11363-1: Gas cylinders — 17E and 25E taper threads for connection of valves to gas cylinders
ISO 15001: Anaesthetic and respiratory equipment – Compatibility with oxygen
| Regional/local standards | Country-specific and regional colour gas coding and other standards apply and must be listed.
| Packaging | Name and/or trade mark and address of the manufacturer.
Product name.
Product reference.
Type of product and main characteristics.
Performance testing information against the mentioned standards.
Lot number prefixed by the word "LOT" (or equivalent harmonised symbol).
Expiry date by year and month, prefixed by the word "EXP" (or equivalent harmonised symbol).
Information for particular storage conditions (temperature, pressure, light, humidity, etc.), as appropriate (or equivalent harmonised symbol), if applicable.
Information for handling, if applicable (or equivalent harmonised symbol).
If the packaging is not transparent, it must bear a diagram (preferably actual size) showing the essential parts of the product and indicating the position of the product in the packaging.
Gross Weight.
Cubic Measurement.
All indicated at least in English.
Extra information required: number of units.