## Introduction
Request for Proposal for , Installation, Testing & Commissioning Medical Oxygen VIE Tanks, Control Panel & Vaporizer
Reference | RFP/CHAI-TZ-EAPOA-002/25
Posting Date | 2026-09-07
Closing date | 2026-09-21
Introduction
The Clinton Health Access Initiative (CHAI) is supporting the strengthening of medical oxygen ecosystems, including the improvement of medical oxygen availability and supply systems in Eastern Africa through support of Unitaid. The East Africa Program on Oxygen Access (EAPOA) aims to improve access to medical oxygen in low- and middle-income countries (LMICs) across East Africa. The initiative seeks to bolster the capacity of local manufacturers to meet the growing demand for medical oxygen.
CHAI intends to use part of the investment from unitaid to cover for installation of Medical Liquid Oxygen Cryogenic storage Tanks.
CHAI invites financial proposals (RFP) from Contractors interested and capable of Installation, Testing & Commissioning liquid Oxygen VIE Tanks , Control Panels and Vaporizers including piping at the following Hospitals in mainland Tanzania;
Bidders may respond and Submit their proposal for all or selected facilities.
1 | Mbeya Regional Referral Hospital
2 | Morogoro Regional Referral Hospital
3 | Songea Regional Referral Hospital
4 | Manyara Regional Referral Hospital
5 | Dodoma Regional Referral Hospital
The purpose of this Request for Proposal is to:
· Provide information to potential suppliers on CHAI’s needs and requirements.
· Solicit information from potential contractor on their capacity, current lead times, pricing, and other information pertinent to procurement planning.
· Evaluate submissions to identify and shortlist qualified potential contractor.
Submissions
Interested organizations must submit their RFP (electronically) to the email ID chaitzprocurement@clintonhealthaccess.org quoting RFP/CHAI-TZ-EAPOA-002/25 in the subject line no later than 16th September 2026.
For any clarification / queries please write to us at chaitzprocurement@clintonhealthaccess.org with RFP reference number in the subject line by 23rd May 2025. CHAI may contact respondents for further discussions regarding submissions and subsequent procurement.
Project site Visit: Vendor may visit the site for verification of the site Between September 10th and 15th, 2026. Vendor should communicate with CHAI for better coordination and introduction to the respective hospital prior to the visit date via chaitzprocurement@clintonhealthacceess.org at least two days prior to the visit with subject "Request for project site visit".
Should your submission exceed 2Mb and cannot be sent by email, send an email to request an upload link with the subject ‘Requesting upload link’ to chaitzprocurement@clintonhealthaccess.org.
Submissions received after the deadline will not be considered.
Disclaimer
Distribution of this document does not mean there is any commitment on the part of CHAI to engage any entity. CHAI will not reimburse or otherwise bear any costs associated with this RFP. No fee is charged for the submission of this RFP. All material received in the response to this RFP shall become the property of CHAI and will not be returned to the respondent. CHAI reserves the right to use any information presented in any proposal.
CHAI code of conduct for suppliers
The CHAI code of conduct for suppliers is a minimum set of requirements that suppliers must meet to qualify to do business with CHAI and remain in good standing with the organization. Please read the document via this link: https://clintonhealth.app.box.com/s/w4aev9ayvkwkklonlkrz45oab80s2ero Supplier Code of Conduct and apply for this solicitation only if your organization can comply with these requirements.
Contract Price
This will be a fixed price contract based on the priced Bills of Quantities and actual quantities measured at site. All the prices should be quoted in Tsh

## Eligibility Criteria
# | Category | Criterion | Requirement
1 | 2.1 Relevant Company Experience | Track record | Carried out works of a similar nature — supply, installation, testing and/or commissioning of liquid oxygen storage tanks (VIE) or comparable medical/industrial gas storage systems — within the last 5 years.
2 | 2.1 Relevant Company Experience | Minimum volume of experience | Provide a list of at least 3 similar projects completed in the last 5 years, including client name, contract value, scope of work, and completion date.
3 | 2.1 Relevant Company Experience | Proof of performance | Verifiable evidence of satisfactory performance for each reference project (client completion certificates, commissioning reports, or signed reference letters). Self-declarations without supporting evidence will not be accepted.
4 | 2.2 Qualified Technical Personnel | Experience requirement | Field qualified personnel with a minimum of 5 years of hands-on experience in the lifting, installation, testing and commissioning of liquid oxygen (VIE) tanks.
5 | 2.2 Qualified Technical Personnel | Key personnel to be named | At minimum, name a Lead Installation/Commissioning Engineer and a Health, Safety and Environment (HSE) focal person, each with relevant cryogenic/medical gas experience.
6 | 2.2 Qualified Technical Personnel | Curriculum Vitae (CV) | Submit CVs for all proposed key technical personnel, listing qualifications, relevant certifications, years of experience, and specific reference projects (with the individual's role on each).
7 | 2.3 Certification for Medical Gas Installation Works | Certification | The bidder (as a company) must be certified or otherwise formally authorized to undertake medical gas pipeline and storage installation works, with specific competence in VIE tank installation.
8 | 2.3 Certification for Medical Gas Installation Works | Standards compliance | Works must comply with applicable medical gas and cryogenic storage standards (e.g. ISO 7396-1, EIGA guidelines, or equivalent) and Tanzania's applicable regulatory requirements for medical gas installations.
9 | 2.4 Servicing, Maintenance & After-Installation Support | Servicing experience | Demonstrate prior experience in servicing and preventive/corrective maintenance of liquid oxygen (VIE) tanks and associated vaporizers, manifolds and alarm systems.
10 | 2.4 Servicing, Maintenance & After-Installation Support | After-installation capacity | Describe capacity to provide after-installation services, including proposed warranty period, availability of spare parts, and response time commitments for breakdowns.
11 | 2.5 Legal, Financial & Regulatory Standing | Registration | Provide a valid certificate of business/company registration (and, where applicable, tax registration/compliance certificate).
12 | 2.5 Legal, Financial & Regulatory Standing | Financial capacity | Demonstrate adequate financial capacity to execute the contract, e.g. through audited financial statements or a bank reference letter.
13 | 2.5 Legal, Financial & Regulatory Standing | Insurance | Confirm ability to provide relevant insurance cover (e.g. contractor's all-risk, public liability) for the duration of the works.
14 | 2.5 Legal, Financial & Regulatory Standing | Good standing | Must not be under a declaration of ineligibility or debarment by any government, donor, or international organization; must declare any conflict of interest.
15 | 2.6 Health, Safety and Quality | HSE plan | Submit an outline Health, Safety and Environment (HSE) plan specific to the lifting, installation and commissioning of cryogenic liquid oxygen tanks.
16 | 2.6 Health, Safety and Quality | Quality assurance | Describe quality assurance/quality control approach to installation, pressure testing and commissioning.
17 | 2.7 Eligibility of Bidders Registered Outside Tanzania | Mobilization | Confirm ability to mobilize personnel and equipment into Tanzania, including any work permits, visas, or import clearances required.
18 | 2.7 Eligibility of Bidders Registered Outside Tanzania | Import/regulatory compliance | Confirm compliance with all applicable Tanzanian import, customs and regulatory requirements for medical gas equipment.
Mandatory Documents to be Submitted
• Certificate of company registration and tax compliance certificate.
• List of at least 3 similar completed projects in the last 5 years, with client contacts.
• Proof of performance for each reference project (completion certificates, commissioning reports, or client reference letters).
• Certification/authorization to undertake medical gas installation works, specifically VIE tank installation.
• CVs of all proposed key technical personnel, with certifications and reference projects.
• Evidence of servicing/maintenance experience and description of proposed after-installation support and warranty terms.
• Outline HSE plan for lifting, installation, testing and commissioning of liquid oxygen tanks.
• Evidence of financial capacity (audited accounts or bank reference letter) and proof of insurance capability.
• For bidders registered outside Tanzania: a statement addressing the requirements in Section 2.7.
• Signed self-declaration of eligibility and absence of conflict of interest.

## Summary
| REFERENCE NUMBER | RFP/CHAI-TZ-EAPOA-002/25
Price
Item | Healthcare Facility | VIE Tank Installation | mLOX for Commissioning | Total | Delivery Period (WKS) | Comments
1 | Dodoma Regional Referral Hospital | 0 | 0 | 0
2 | Manyara Regional Referral Hospital | 0 | 0 | 0
3 | Songea Regional Referral Hospital | 0 | 0 | 0
4 | Morogoro Regional Referral Hospital | 0 | 0 | 0
5 | Mbeya Regional Referral Hospital | 0 | 0 | 0
| Total RFP SUM TSH | 0 | 0 | 0

## MBEYA RRH
| VIE TANK INSTALLATION |  |  | MBEYA RRH
| REFERENCE NUMBER | RFP/CHAI-TZ-EAPOA-002/25
No. | DESCRIPTION (Section A) | QTY | UNIT | RATE | AMOUNT
1 | Piping (Copper pipe manufactured from phosphorus de-oxidized non-arsenical copper to conform to BS EN HTM02-01)
| 22mm diameter degreased copper pipes in metres | 58 | LM |  | 0
2 | Piping Accessories Straight Couplers:
| 22mm diameter degreased copper straight couplers | 30 | Pcs |  | 0
3 | Elbows:
| 22mm diameter degreased copper elbows | 30 | Pcs |  | 0
4 | Reducers:
| 28x22mm diameter degreased copper reducer | 2 | Pcs |  | 0
| 22x15mm diameter degreased copper reducer | 4 | Pcs |  | 0
5 | Line ball valves c/w NIST (Medical gas line valves conforming to HTM 02-01)
| 22mm medical gas line valves | 1 | Item |  | 0
| 15mm medical gas line valves | 1 | Item |  | 0
| 22mm medical gas line Non Return valves | 2 | Item |  | 0
| 15mm medical gas line Non Return valves | 2 | Item |  | 0
| Total Collection on Section A |  |  |  | 0
Page 1 of 2
REFERENCE NUMBER
No. | DESCRIPTION (Section B) | QTY | UNIT | RATE | AMOUNT
6 | Mounting accessories
| 22mm munsen rings complete with clamps | 30 | Item |  | 0
| M10 threaded rod | 3 | LM |  | 0
| M10 hungers | 60 | no |  | 0
7 | Lifting & Cranage , Tansportation and Installation of the Liquid Oxygen VIE Tank ,10,000 Litres Capacity (Empty Weight - 5 Tons-Diameter-2.5m-Height- 6m) | 1 | Sum |  | 0
8 | Anchor bolts(M10 raw bolts -12 No. , Control Panel Mounting Frames ( 304 Stainless angle line 50x50x2.5mm) LXWXH-(1200x300x900) with cross members to be mounted on the plinth using M1O Raw bolts. | 1 | Sum |  | 0
9 | Power Provision Single Phase, Twin Socket 240V, 50Hz( Cable size 6 mm2) | 50 | LM |  | 0
10 | Labour Cost (Installation, Testing & Commissioning) | 1 | Item |  | 0
11 | Provision of at least 2 appropriate Fire Extinguishers (Carbon Dioxide or Dry Chemical type) to be placed/anchored nearby the VIE system | 1 | Sum |  | 0
12 | VIE Tank Earthing | 1 | Item |  | 0
13 | Inlet /outlet Vaporizer Flange DN 25PN40 NPS 1" Complete with PTFE gasket to make the Joint leak proof. | 4 | Item |  | 0
14 | Provison of Medical oxygen safety signs board measuring 600mmx450 UV reflective | 1 | Item |  | 0
15 | Provison of 1200mmx600 UV reflective UNITAID reflective logo-design to be provided by CHAI | 1 | Item |  | 0
| Total Collection on Section B |  |  |  | 0
No. | DESCRIPTION (Section C) | QTY | UNIT | RATE | AMOUNT
16 | mLOX for Commissioning the system | 500 | Kg |  | 0
| Total Collection on Section C |  |  |  | 0
Collection:
| Total brought forward from Section A |  |  |  | 0
| Total brought down from Section B |  |  |  | 0
| Total (Sections A+B) |  |  |  | 0
| Add 18% VAT |  |  |  | 0
| Grand Total (Sections A+B+C) |  |  |  | 0
Amount in Words:
______________________________________________
| Tenderer's Name: | ______________________
| Sign & Stamp: ___________________________________ Date: |  |  | ___________ 2026
Witness Name: ________________________
Sign: _______________________________

## MOROGORO RRH
| VIE TANK INSTALLATION |  |  | MOROGORO RRH
| REFERENCE NUMBER | RFP/CHAI-TZ-EAPOA-002/25
No. | DESCRIPTION (Section A) | QTY | UNIT | RATE | AMOUNT
1 | Piping (Copper pipe manufactured from phosphorus de-oxidized non-arsenical copper to conform to BS EN HTM02-01)
| 22mm diameter degreased copper pipes in metres | 58 | LM |  | 0
2 | Piping Accessories Straight Couplers:
| 22mm diameter degreased copper straight couplers | 30 | Pcs |  | 0
3 | Elbows:
| 22mm diameter degreased copper elbows | 30 | Pcs |  | 0
4 | Reducers:
| 28x22mm diameter degreased copper reducer | 2 | Pcs |  | 0
| 22x15mm diameter degreased copper reducer | 4 | Pcs |  | 0
5 | Line ball valves c/w NIST (Medical gas line valves conforming to HTM 02-01)
| 22mm medical gas line valves | 1 | Item |  | 0
| 15mm medical gas line valves | 1 | Item |  | 0
| 22mm medical gas line Non Return valves | 2 | Item |  | 0
| 15mm medical gas line Non Return valves | 2 | Item |  | 0
| Total Collection on Section A |  |  |  | 0
Page 1 of 2
REFERENCE NUMBER
No. | DESCRIPTION (Section B) | QTY | UNIT | RATE | AMOUNT
6 | Mounting accessories
| 22mm munsen rings complete with clamps | 30 | Item |  | 0
| M10 threaded rod | 3 | LM |  | 0
| M10 hungers | 60 | no |  | 0
7 | Lifting & Cranage , Tansportation and Installation of the Liquid Oxygen VIE Tank ,10,000 Litres Capacity (Empty Weight - 5 Tons-Diameter-2.5m-Height- 6m) | 1 | Sum |  | 0
8 | Anchor bolts(M10 raw bolts -12 No. , Control Panel Mounting Frames ( 304 Stainless angle line 50x50x2.5mm) LXWXH-(1200x300x900) with cross members to be mounted on the plinth using M1O Raw bolts. | 1 | Sum |  | 0
9 | Power Provision Single Phase, Twin Socket 240V, 50Hz( Cable size 6 mm2) | 50 | LM |  | 0
10 | Labour Cost (Installation, Testing & Commissioning) | 1 | Item |  | 0
11 | Provision of at least 2 appropriate Fire Extinguishers (Carbon Dioxide or Dry Chemical type) to be placed/anchored nearby the VIE system | 1 | Sum |  | 0
12 | VIE Tank Earthing | 1 | Item |  | 0
13 | Inlet /outlet Vaporizer Flange DN 25PN40 NPS 1" Complete with PTFE gasket to make the Joint leak proof. | 4 | Item |  | 0
14 | Provison of Medical oxygen safety signs board measuring 600mmx450 UV reflective | 1 | Item |  | 0
15 | Provison of 1200mmx600 UV reflective UNITAID reflective logo-design to be provided by CHAI | 1 | Item |  | 0
| Total Collection on Section B |  |  |  | 0
No. | DESCRIPTION (Section C) | QTY | UNIT | RATE | AMOUNT
16 | mLOX for Commissioning the system | 500 | Kg |  | 0
| Total Collection on Section C |  |  |  | 0
Collection:
| Total brought forward from Section A |  |  |  | 0
| Total brought down from Section B |  |  |  | 0
| Total (Sections A+B) |  |  |  | 0
| Add 18% VAT |  |  |  | 0
| Grand Total (Sections A+B+C) |  |  |  | 0
Amount in Words:
______________________________________________
| Tenderer's Name: | ______________________
| Sign & Stamp: ___________________________________ Date: |  |  | ___________ 2026
Witness Name: ________________________
Sign: _______________________________

## SONGEA RRH
| VIE TANK INSTALLATION |  |  | SONGEA RRH
| REFERENCE NUMBER | RFP/CHAI-TZ-EAPOA-002/25
No. | DESCRIPTION (Section A) | QTY | UNIT | RATE | AMOUNT
1 | Piping (Copper pipe manufactured from phosphorus de-oxidized non-arsenical copper to conform to BS EN HTM02-01)
| 22mm diameter degreased copper pipes in metres | 58 | LM |  | 0
2 | Piping Accessories Straight Couplers:
| 22mm diameter degreased copper straight couplers | 30 | Pcs |  | 0
3 | Elbows:
| 22mm diameter degreased copper elbows | 30 | Pcs |  | 0
4 | Reducers:
| 28x22mm diameter degreased copper reducer | 2 | Pcs |  | 0
| 22x15mm diameter degreased copper reducer | 4 | Pcs |  | 0
5 | Line ball valves c/w NIST (Medical gas line valves conforming to HTM 02-01)
| 22mm medical gas line valves | 1 | Item |  | 0
| 15mm medical gas line valves | 1 | Item |  | 0
| 22mm medical gas line Non Return valves | 2 | Item |  | 0
| 15mm medical gas line Non Return valves | 2 | Item |  | 0
| Total Collection on Section A |  |  |  | 0
Page 1 of 2
REFERENCE NUMBER
No. | DESCRIPTION (Section B) | QTY | UNIT | RATE | AMOUNT
6 | Mounting accessories
| 22mm munsen rings complete with clamps | 30 | Item |  | 0
| M10 threaded rod | 3 | LM |  | 0
| M10 hungers | 60 | no |  | 0
7 | Lifting & Cranage , Tansportation and Installation of the Liquid Oxygen VIE Tank ,10,000 Litres Capacity (Empty Weight - 5 Tons-Diameter-2.5m-Height- 6m) | 1 | Sum |  | 0
8 | Anchor bolts(M10 raw bolts -12 No. , Control Panel Mounting Frames ( 304 Stainless angle line 50x50x2.5mm) LXWXH-(1200x300x900) with cross members to be mounted on the plinth using M1O Raw bolts. | 1 | Sum |  | 0
9 | Power Provision Single Phase, Twin Socket 240V, 50Hz( Cable size 6 mm2) | 50 | LM |  | 0
10 | Labour Cost (Installation, Testing & Commissioning) | 1 | Item |  | 0
11 | Provision of at least 2 appropriate Fire Extinguishers (Carbon Dioxide or Dry Chemical type) to be placed/anchored nearby the VIE system | 1 | Sum |  | 0
12 | VIE Tank Earthing | 1 | Item |  | 0
13 | Inlet /outlet Vaporizer Flange DN 25PN40 NPS 1" Complete with PTFE gasket to make the Joint leak proof. | 4 | Item |  | 0
14 | Provison of Medical oxygen safety signs board measuring 600mmx450 UV reflective | 1 | Item |  | 0
15 | Provison of 1200mmx600 UV reflective UNITAID reflective logo-design to be provided by CHAI | 1 | Item |  | 0
| Total Collection on Section B |  |  |  | 0
No. | DESCRIPTION (Section C) | QTY | UNIT | RATE | AMOUNT
16 | mLOX for Commissioning the system | 500 | Kg |  | 0
| Total Collection on Section C |  |  |  | 0
Collection:
| Total brought forward from Section A |  |  |  | 0
| Total brought down from Section B |  |  |  | 0
| Total (Sections A+B) |  |  |  | 0
| Add 18% VAT |  |  |  | 0
| Grand Total (Sections A+B+C) |  |  |  | 0
Amount in Words:
______________________________________________
| Tenderer's Name: | ______________________
| Sign & Stamp: ___________________________________ Date: |  |  | ___________ 2026
Witness Name: ________________________
Sign: _______________________________

## MANYARA RRH
| VIE TANK INSTALLATION |  |  | MANYARA RRH
| REFERENCE NUMBER | RFP/CHAI-TZ-EAPOA-002/25
No. | DESCRIPTION (Section A) | QTY | UNIT | RATE | AMOUNT
1 | Piping (Copper pipe manufactured from phosphorus de-oxidized non-arsenical copper to conform to BS EN HTM02-01)
| 22mm diameter degreased copper pipes in metres | 58 | LM |  | 0
2 | Piping Accessories Straight Couplers:
| 22mm diameter degreased copper straight couplers | 30 | Pcs |  | 0
3 | Elbows:
| 22mm diameter degreased copper elbows | 30 | Pcs |  | 0
4 | Reducers:
| 28x22mm diameter degreased copper reducer | 2 | Pcs |  | 0
| 22x15mm diameter degreased copper reducer | 4 | Pcs |  | 0
5 | Line ball valves c/w NIST (Medical gas line valves conforming to HTM 02-01)
| 22mm medical gas line valves | 1 | Item |  | 0
| 15mm medical gas line valves | 1 | Item |  | 0
| 22mm medical gas line Non Return valves | 2 | Item |  | 0
| 15mm medical gas line Non Return valves | 2 | Item |  | 0
| Total Collection on Section A |  |  |  | 0
Page 1 of 2
REFERENCE NUMBER
No. | DESCRIPTION (Section B) | QTY | UNIT | RATE | AMOUNT
6 | Mounting accessories
| 22mm munsen rings complete with clamps | 30 | Item |  | 0
| M10 threaded rod | 3 | LM |  | 0
| M10 hungers | 60 | no |  | 0
7 | Lifting & Cranage , Tansportation and Installation of the Liquid Oxygen VIE Tank ,10,000 Litres Capacity (Empty Weight - 5 Tons-Diameter-2.5m-Height- 6m) | 1 | Sum |  | 0
8 | Anchor bolts(M10 raw bolts -12 No. , Control Panel Mounting Frames ( 304 Stainless angle line 50x50x2.5mm) LXWXH-(1200x300x900) with cross members to be mounted on the plinth using M1O Raw bolts. | 1 | Sum |  | 0
9 | Power Provision Single Phase, Twin Socket 240V, 50Hz( Cable size 6 mm2) | 50 | LM |  | 0
10 | Labour Cost (Installation, Testing & Commissioning) | 1 | Item |  | 0
11 | Provision of at least 2 appropriate Fire Extinguishers (Carbon Dioxide or Dry Chemical type) to be placed/anchored nearby the VIE system | 1 | Sum |  | 0
12 | VIE Tank Earthing | 1 | Item |  | 0
13 | Inlet /outlet Vaporizer Flange DN 25PN40 NPS 1" Complete with PTFE gasket to make the Joint leak proof. | 4 | Item |  | 0
14 | Provison of Medical oxygen safety signs board measuring 600mmx450 UV reflective | 1 | Item |  | 0
15 | Provison of 1200mmx600 UV reflective UNITAID reflective logo-design to be provided by CHAI | 1 | Item |  | 0
| Total Collection on Section B |  |  |  | 0
No. | DESCRIPTION (Section C) | QTY | UNIT | RATE | AMOUNT
16 | mLOX for Commissioning the system | 500 | Kg |  | 0
| Total Collection on Section C |  |  |  | 0
Collection:
| Total brought forward from Section A |  |  |  | 0
| Total brought down from Section B |  |  |  | 0
| Total (Sections A+B) |  |  |  | 0
| Add 18% VAT |  |  |  | 0
| Grand Total (Sections A+B+C) |  |  |  | 0
Amount in Words:
______________________________________________
| Tenderer's Name: | ______________________
| Sign & Stamp: ___________________________________ Date: |  |  | ___________ 2026
Witness Name: ________________________
Sign: _______________________________

## DODOMA RRH
| VIE TANK INSTALLATION |  |  | DODOMA RRH
| REFERENCE NUMBER | RFP/CHAI-TZ-EAPOA-002/25
No. | DESCRIPTION (Section A) | QTY | UNIT | RATE | AMOUNT
1 | Piping (Copper pipe manufactured from phosphorus de-oxidized non-arsenical copper to conform to BS EN HTM02-01)
| 22mm diameter degreased copper pipes in metres | 58 | LM |  | 0
2 | Piping Accessories Straight Couplers:
| 22mm diameter degreased copper straight couplers | 30 | Pcs |  | 0
3 | Elbows:
| 22mm diameter degreased copper elbows | 30 | Pcs |  | 0
4 | Reducers:
| 28x22mm diameter degreased copper reducer | 2 | Pcs |  | 0
| 22x15mm diameter degreased copper reducer | 4 | Pcs |  | 0
5 | Line ball valves c/w NIST (Medical gas line valves conforming to HTM 02-01)
| 22mm medical gas line valves | 1 | Item |  | 0
| 15mm medical gas line valves | 1 | Item |  | 0
| 22mm medical gas line Non Return valves | 2 | Item |  | 0
| 15mm medical gas line Non Return valves | 2 | Item |  | 0
| Total Collection on Section A |  |  |  | 0
Page 1 of 2
REFERENCE NUMBER
No. | DESCRIPTION (Section B) | QTY | UNIT | RATE | AMOUNT
6 | Mounting accessories
| 22mm munsen rings complete with clamps | 30 | Item |  | 0
| M10 threaded rod | 3 | LM |  | 0
| M10 hungers | 60 | no |  | 0
7 | Lifting & Cranage , Tansportation and Installation of the Liquid Oxygen VIE Tank ,10,000 Litres Capacity (Empty Weight - 5 Tons-Diameter-2.5m-Height- 6m) | 1 | Sum |  | 0
8 | Anchor bolts(M10 raw bolts -12 No. , Control Panel Mounting Frames ( 304 Stainless angle line 50x50x2.5mm) LXWXH-(1200x300x900) with cross members to be mounted on the plinth using M1O Raw bolts. | 1 | Sum |  | 0
9 | Power Provision Single Phase, Twin Socket 240V, 50Hz( Cable size 6 mm2) | 50 | LM |  | 0
10 | Labour Cost (Installation, Testing & Commissioning) | 1 | Item |  | 0
11 | Provision of at least 2 appropriate Fire Extinguishers (Carbon Dioxide or Dry Chemical type) to be placed/anchored nearby the VIE system | 1 | Sum |  | 0
12 | VIE Tank Earthing | 1 | Item |  | 0
13 | Inlet /outlet Vaporizer Flange DN 25PN40 NPS 1" Complete with PTFE gasket to make the Joint leak proof. | 4 | Item |  | 0
14 | Provison of Medical oxygen safety signs board measuring 600mmx450 UV reflective | 1 | Item |  | 0
15 | Provison of 1200mmx600 UV reflective UNITAID reflective logo-design to be provided by CHAI | 1 | Item |  | 0
| Total Collection on Section B |  |  |  | 0
No. | DESCRIPTION (Section C) | QTY | UNIT | RATE | AMOUNT
16 | mLOX for Commissioning the system | 500 | Kg |  | 0
| Total Collection on Section C |  |  |  | 0
Collection:
| Total brought forward from Section A |  |  |  | 0
| Total brought down from Section B |  |  |  | 0
| Total (Sections A+B) |  |  |  | 0
| Add 18% VAT |  |  |  | 0
| Grand Total (Sections A+B+C) |  |  |  | 0
Amount in Words:
______________________________________________
| Tenderer's Name: | ______________________
| Sign & Stamp: ___________________________________ Date: |  |  | ___________ 2026
Witness Name: ________________________
Sign: _______________________________

## REFERENCES
PROJECTS OF SIMILAR NATURE
Item | Project Name | Client | Project Amount | Project Status | Contact Person Name | Email Contact | Tel Contact
1
2
3
4
5
6
7
8
9
10
Notes
Provide proof of performance ;LPOS, Contracts