THE CLINTON HEALTH ACCESS INITIATIVE (CHAI)

PROPOSED PROJECT FOR INSTALLATION OF VACUUM-INSULATED EVAPORATOR (VIE) TANKS AND VAPORIZERS IN TEN HOSPITALS IN MAINLAND TANZANIA

BIDDING DOCUMENT FOR INSTALLATION OF VIE TANKS, CONTROL PANELS, VAPORIZERS AND PIPING

UNITAID SUPPORT

Issued by:

CHAI

SEPTEMBER 2026

INSTRUCTIONS TO BIDDERS (ITBs)

- PREAMBLE

The Clinton Health Access Initiative (CHAI) is supporting the strengthening of medical oxygen ecosystems, including the improvement of medical oxygen availability and supply systems in Eastern Africa through support of UNITAID.  The East Africa Program on Oxygen Access (EAPOA) aims to improve access to medical oxygen in low- and middle-income countries (LMICs) across East Africa. The initiative seeks to bolster the capacity of local manufacturers to meet the growing demand for medical oxygen.

CHAI intends to use part of the proceeds to cover for installation of Vacuum-Insulated Evaporator (VIE) Tanks, Control Panels, Vaporizers and Piping for the following five (5) hospitals in Mainland Tanzania: -

- Dodoma Regional Referral Hospital (DRRH) in Dodoma.

- Manyara (MRRH) in Manyara.

- Songea RRH in Ruvuma.

- Morogoro RRH in Morogoro, and

- Mbeya RRH in Mbeya

The VIE-Tanks, Control-Panels and Vaporizers were purchased and stored at Chang’ombe-area in DAR ES SALAAM by CHAI. Also, the plinths/slabs have already been constructed by another Vendor.

In collaboration with Expert-Team, Ministry of Health and, Hospital Biomedical Engineering Teams, CHAI has planned that the project will include the following seven (7) main tasks: -

- Tasks mobilization which will also involve setting timelines for resources-availability, loading, transportation, unloading, piping complete with accessories, testing, third-part-inspection and commissioning.

- Transportation complete with truck, loading and unloading of VIE-Tank and Vaporizer from Chang’ombe-area in DAR ES SALAAM to the respective site.

- Ensuring VIE-Tank, Vaporizer and Control-Panel are in appropriate place on the plinth/slab in line with schematic drawings and HTM-02-01 Standards and requirements.

- Piping from VIE-Tank to Vaporizer and Manifold.

- Testing the piping and connections in line with HTM-02-01 standards and requirements.

- Piping-inspection by Third-Party-Inspector.

- Documentations and Commissioning.

This document provides the technical and commercial specifications for the VIE-Tanks cum Vaporizers transportation, installation and commissioning of the VIE system.

- TENDERING METHOD

The Bid is open to any Local or International Bidder incorporated in the respective country.

The Bidder is allowed to bid for any number (1-5) of bids subject to capability, timely implementation and appropriate methodology: -

| BID No. | AVAILABLE BIDS | LOCATION |
| --- | --- | --- |
| 1 | Morogoro RRH | MOROGORO |
| 2 | Manyara RRH | MANYARA |
| 3 | Songea RRH | RUVUMA |
| 4 | Dodoma RRH | DODOMA |
| 5 | Mbeya RRH | MBEYA |

Bidders are invited to bid for single or more than one Bid in line with the Instructions to Bidders

- LANGUAGE AND CURRENCY OF BID

The language of Bid is English and, pricing must be in Tanzanian Shillings or in Foreign-Currency at the mean-exchange rate issued by Bank of Tanzania on the Bid-Opening-Date.

- CLARIFICATIONS OF BID

For any clarification / queries please write to us at chaitzprocurement@clintonhealthaccess.org; with bid reference number in the subject line by September 16th, 2026. CHAI may contact respondents for further discussions regarding submissions and subsequent procurement.

- SCOPE OF WORKS

Generally, the VIE-Tanks require Lifting and Cranage, Transportation and Installation of the Liquid Oxygen VIE Tank, 10,000 Liters Capacity (Empty Weight - 5 Tons-Diameter-2.5m-Height- 6m) also, lifting of Vaporizers and Control-Panels .

The successful Bidder will specifically be required to undertake the following tasks: -

- Transportation by truck, loading and unloading of VIE-Tank, Vaporizer and Control-Panels from Chang’ombe-area in DAR ES SALAAM to the respective sites;

- Supplying and Installation of Copper-Pipes complete with accessories in line with Schedule of Works (Bills of Quantities) to conform to BS EN HTM02-01.

- Powering the system with Single Phase, Twin Socket 240V, 50Hz (Cable size 6 mm2) (provisional).

- Provision of at least 2 appropriate Fire Extinguishers (Carbon Dioxide or Dry Chemical type) to be placed/anchored nearby the VIE system.

- VIE Tank Earthing.

- COLLABORATIONS

- The Plinth/Slab for VIE-Tank was constructed by another Vendor;

- The successful Bidder will also be obliged to touch base with sole-supplier of mLOX in Tanzania (M/S TOL Gases PLC);

- CHAI and Team of Experts.

- Third (3rd) Party Inspector on piping-installation.

- TYPE OF CONTRACT

This contract will be a direct contract to be executed by the successful Vendor and CHAI who will be the “Employer”.

The standard CHAI procedure for appointment will be used. The appointment will be done according to the internal manual and policy. The standard Purchase Order (PO) complete with relevant schematic-drawings, specifications and blank-work-schedule or Bills of Quantities (BOQs) is attached with this bidding-document for easy reference, pricing and contract appointment document. CHAI and Expert-Team will act as the Engineer and Principal Agent. The Principal Agent shall make provision for and purchase the above documents.

- BID ELIGIBILITY

This is an open Bid to all local and international prospective vendors whom can meet the HTM-02-01 Standards.

The Bid will be issued to any International or Local Legal and experienced Vendor with proof of legal-incorporation and experience of similar assignment.

| # | Category | Criterion | Requirement |
| --- | --- | --- | --- |
| 1 | 2.1 Relevant Company Experience | Track record | Carried out works of a similar nature — supply, installation, testing and/or commissioning of liquid oxygen storage tanks (VIE) or comparable medical/industrial gas storage systems — within the last 5 years. |
| 2 | 2.1 Relevant Company Experience | Minimum volume of experience | Provide a list of at least 3 similar projects completed in the last 5 years, including client name, contract value, scope of work, and completion date. |
| 3 | 2.1 Relevant Company Experience | Proof of performance | Verifiable evidence of satisfactory performance for each reference project (client completion certificates, commissioning reports, or signed reference letters). Self-declarations without supporting evidence will not be accepted. |
| 4 | 2.2 Qualified Technical Personnel | Experience requirement | Field qualified personnel with a minimum of 5 years of hands-on experience in the lifting, installation, testing and commissioning of liquid oxygen (VIE) tanks. |
| 5 | 2.2 Qualified Technical Personnel | Key personnel to be named | At minimum, name a Lead Installation/Commissioning Engineer and a Health, Safety and Environment (HSE) focal person, each with relevant cryogenic/medical gas experience. |
| 6 | 2.2 Qualified Technical Personnel | Curriculum Vitae (CV) | Submit CVs for all proposed key technical personnel, listing qualifications, relevant certifications, years of experience, and specific reference projects (with the individual's role on each). |
| 7 | 2.3 Certification for Medical Gas Installation Works | Certification | The bidder (as a company) must be certified or otherwise formally authorized to undertake medical gas pipeline and storage installation works, with specific competence in VIE tank installation. |
| 8 | 2.3 Certification for Medical Gas Installation Works | Standards compliance | Works must comply with applicable medical gas and cryogenic storage standards (e.g. ISO 7396-1, EIGA guidelines, or equivalent) and Tanzania's applicable regulatory requirements for medical gas installations. |
| 9 | 2.4 Servicing, Maintenance & After-Installation Support | Servicing experience | Demonstrate prior experience in servicing and preventive/corrective maintenance of liquid oxygen (VIE) tanks and associated vaporizers, manifolds and alarm systems. |
| 10 | 2.4 Servicing, Maintenance & After-Installation Support | After-installation capacity | Describe capacity to provide after-installation services, including proposed warranty period, availability of spare parts, and response time commitments for breakdowns. |
| 11 | 2.5 Legal, Financial & Regulatory Standing | Registration | Provide a valid certificate of business/company registration (and, where applicable, tax registration/compliance certificate). |
| 12 | 2.5 Legal, Financial & Regulatory Standing | Financial capacity | Demonstrate adequate financial capacity to execute the contract, e.g. through audited financial statements or a bank reference letter. |
| 13 | 2.5 Legal, Financial & Regulatory Standing | Insurance | Confirm ability to provide relevant insurance cover (e.g. contractor's all-risk, public liability) for the duration of the works. |
| 14 | 2.5 Legal, Financial & Regulatory Standing | Good standing | Must not be under a declaration of ineligibility or debarment by any government, donor, or international organization; must declare any conflict of interest. |
| 15 | 2.6 Health, Safety and Quality | HSE plan | Submit an outline Health, Safety and Environment (HSE) plan specific to the lifting, installation and commissioning of cryogenic liquid oxygen tanks. |
| 16 | 2.6 Health, Safety and Quality | Quality assurance | Describe quality assurance/quality control approach to installation, pressure testing and commissioning. |
| 17 | 2.7 Eligibility of Bidders Registered Outside Tanzania | Mobilization | Confirm ability to mobilize personnel and equipment into Tanzania, including any work permits, visas, or import clearances required. |
| 18 | 2.7 Eligibility of Bidders Registered Outside Tanzania | Import/regulatory compliance | Confirm compliance with all applicable Tanzanian import, customs and regulatory requirements for medical gas equipment. |

- EVALUATION AND ADJUDICATION

The Bid will be evaluated and adjudicated by Evaluation-Committee, CHAI-Procurement and, Adjudication by CHAI-Management as per approved CHAI’s Procurement Policy.

A written recommendation will be made to CHAI-Procurement who will review the recommendation against their procurement policy and, advise the CHAI-Management for a final appointment. The appointment will be awarded based on local content, completeness of document submission (proving competency and capability) and price according to the following formula:

| Description | Percentage |
| --- | --- |
| Local Content – Locally incorporated Vendor with more than three (3) years in the business. | 10% |
| Completeness – of submission of the following compulsory documents: - - Certificate of Incorporation as issued by BRELA; - Power of Attorney for the Authorizing Person; - Taxation Clearance from respective authority; - Current Business License; - Banking details – statements, possibility of credit-facilities and Account Number and Name; - Proof of Registered Address; - Complete priced Bills of Quantities (BOQs) initialed in all pages; - List of similar projects completed over the past 3-years by showing the title, location, client name, consultant and, value; - List of projects underway; - Program of Work - Method Statement | 10% |
| Technical Competency to all sites: - - Past-experience in terms of similar projects in value and complexity completed over the past three years; - Project Duration - Workable Methodology to substantiate timely operations; - Availability of qualified Mechanical or Biomedical Engineers, Piping-Technicians, Electrical-Technicians and Biomedical-Technicians for the assignments; - Availability of Working tools and equipment for the assignments; | 50% |
| Financial Competency – Price | 30% |
| TOTAL | 100% |

- REQUIRED BIDDER COMPETENCY

Only submissions from companies with proven capability and competence will be considered;

- An Incorporated Vendor, with all attachments under chapter nine (9) above with completeness of submissions of items a) to k).

- Be able to demonstrate technical-competence under chapter nine (9) above with in items a) to e).

- Cost-effective-offer.

- CONTRACT PRICE

This will be a fixed price contract based on the priced Bills of Quantities.

- EXTRA PAYMENTS

Vendors must acquaint themselves fully with the local conditions of the sites and the requirements of the specifications. CHAI will not consider any later claims by the successful Vendors for extra payment arising out of underestimating any of the requirements.

- PROGRAM AND COMPLETION

The period for completion of the work will be proposed by Vendor in her program of work, reviewed by CHAI and agreed upon by taking the operational requirements of the facility into account.

CHAI shall indicate on the Purchase Order (PO) the contract-days required to complete the project. The PO will be adjusted not to penalize the Vendor due to restriction in access. The Vendor shall state the time, in days, required for completion of the contract in the Priced BOQs and such time will be used as contractual completion time of the project.

- METHOD STATEMENT

The Vendor will be required to prepare a comprehensive Methodology for the implementations to respective sites.

- HEALTH AND SAFETY

The Vendor will adhere to all Health & Safety requirements of the Hospital and CHAI’s Environmental Management and Mitigation Plan and seek relevant permissions timeously to operate in the environment where necessary.

The Vendor shall supply and maintain all safety equipment, personal protective equipment and any other assistance and equipment required to gain access to work areas.

- ACCESS AND CONTROL

The vendor and all other employees will be required to keep a register of time on site and handed to the Expert-Team / CHAI on request.

- PARTICULAR SPECIFICATIONS

The Draft Purchase Order attached with this Bidding Document contains the dossier, particular-specifications and drawings.

Particular-specifications;

- Supply and installation requirements

- Specifications of automatic oxygen change over panel and pipeline system

- Flowmeter specification

- Humidifier Specification

Drawings:

- No changes are to be done to the schematic-drawings without approval.

- All dimensions are in mm unless otherwise stated and/or indicated on the drawing.

- SITE OFFICE

If required by the Vendor, in coordination with CHAI and Hospital-Team she may be provided with site office.

The safekeeping of all equipment and tools shall be the responsibility of the Vendor until the acceptance date.

- HANDLING OF MATERIAL

- The Vendor shall be responsible for providing all the required equipment for the offloading and proper handling of the material on site.

- The Vendor shall be responsible for storing material and equipment on site, without obstructing movements of any facility business related to its daily operations.

- DOCUMENTS APPLICABLE

The following documents should be read in conjunction with this bidding document:

- Draft Purchase Order (PO);

- Schematic Drawings attached to PO;

- Specifications attached to PO;

- Unpriced Bills of Quantities under Annex B.

- INSPECTION AND TESTING

On completion of the installation, the Vendor shall carry out his/her own inspections to ensure that the installation and equipment comply with safety standards before notifying the Experts-Team/CHAI.

The Experts-Team/CHAI will not act as the Vendor's inspector or quality control official but to ensure that the work has been completed and to standard.

The Experts-Team should be notified no less than 5 days before completion for sign-off. No snagging procedure shall apply. Work completion shall be accepted or rejected per section as set out in the Completion-Milestones.

The Vendor will also be required to develop commissioning-documentations and As-Built-Drawings.

- CONTRACT COMPLETION MILESTONES

Sectional Completion and Payment Certificates will be issued once the following has been achieved:

- Installation and commissioning being accepted by the Experts-Team.

Works Completion Works Completion will be issued after:

- All sectional completion certificates have been issued.

- PRICE SCHEDULES

- Vendors are required to submit unit prices as indicated in the “Bill of Quantities”.

- Price to hold firm for ninety (90) days from bid closing date.

- Vendor is also required to submit unit-rates and explanations for any additional works.

- PENALTIES

The following penalties shall be applicable:

- If the Vendor fails to complete the project within the agreed timeline as outlined in the contract and annexed schedule, a penalty of 0.1% of the total contract value will be applied for each day of delay, up to a maximum of 10%. This penalty will be deducted from the final payment of the vendor. Exceptions will only be considered for delays caused by force majeure or other circumstances beyond the supplier's control, subject to CHAI’s approval.

- Failure and disregard to follow instructions issued by the Experts-Team/CHAI may result contract termination.

- This will not be the sole and exclusive remedy available to CHAI.

- SITE VISIT FOR BIDDING PURPOSES

Due to the complexity of this work, a compulsory Pre-Bidding-Meeting will be conducted within the first-week of bidding-process and, optional site visits will be arranged at the end of the week.

Bids from Bidders who did not attend the pre-bidding-meeting will not be considered.

- TERMS AND CONDITIONS

- If successful, the Vendor will follow the normal CHAI procurement process.

- CHAI’s Terms and Conditions stipulated in the draft Purchase Order shall apply.

- COMPULSORY SUBMITTAL DOCUMENTS

- The “Bid Submission Document” completed, initialed on each page and signed.

- Completed Bill of Quantities together with clear rates for all items

- Certificate of Incorporation as issued by BRELA for local-vendors or similar from other nations.

- Bid Form.

- Taxation Clearance.

- Power of Attorney for the Authorizing Person;

- Current Business License;

- Banking details – statements, possibility of credit-facilities and, Account Number and Name;

- Proof of Registered Address;

- Complete priced Bills of Quantities (BOQs) initialed in all pages;

- List of staffs and proof of their qualifications and experiences.

- List of similar projects completed over the past 3-years by showing the title, location, client name, consultant and, value;

- List of projects underway;

- Program of Work

- Method Statement

Mandatory Documents to be Submitted

- Certificate of company registration and tax compliance certificate.

- List of at least 3 similar completed projects in the last 5 years, with client contacts.

- Proof of performance for each reference project (completion certificates, commissioning reports, or client reference letters).

- Certification/authorization to undertake medical gas installation works, specifically VIE tank installation.

- CVs of all proposed key technical personnel, with certifications and reference projects.

- Evidence of servicing/maintenance experience and description of proposed after-installation support and warranty terms.

- Outline HSE plan for lifting, installation, testing and commissioning of liquid oxygen tanks.

- Evidence of financial capacity (audited accounts or bank reference letter) and proof of insurance capability.

- For bidders registered outside Tanzania: a statement addressing the requirements in Section 2.7.

- Signed self-declaration of eligibility and absence of conflict of interest.

- SUBMISSION DATE AND TIME

The completed bid submission must be filled out by hand, scanned and submitted electronically on or before Monday September 21st, 2026 in .pdf to chaitzprocurement@clintonhealthaccess.org by the closing date stated on the returnable document. Also, excel softcopies are required.

No late submissions shall be accepted.

- FORMS

  - Bid Form

To:

We, the undersigned, declare that:

- We have examined and have no reservations to the Bidding Documents, including

- We offer to execute in conformity with the Bidding Documents the following Works: ______________________________________________________________;

- The total price of our Bid, excluding any discounts offered in item (d) below is: ___________________________;

- The discounts offered and the methodology for their application are: __________________________________________________;

- Our bid shall be valid for a period of ________ [insert validity period as specified in days from the date fixed for the bid submission deadline in accordance with the Bidding Documents, and it shall remain binding upon us and may be accepted at any time before the expiration of that period;

- Our firm, including any subcontractors or suppliers for any part of the Contract, have nationalities from eligible countries;

- We, including any subcontractors or suppliers for any part of the contract, do not have any conflict of interest;

- We undertake that, in competing for (and, if the award is made to us, in executing) the above contract, we will strictly observe the laws against fraud and corruption in force in the country of the Employer, as such laws have been listed by the Employer in the bidding documents for this contract.

- We understand that this bid, together with your written acceptance thereof included in your notification of award, shall constitute a binding contract between us, until a formal contract is prepared and executed;

- We understand that you are not bound to accept the lowest evaluated bid or any other bid that you may receive; and

- If awarded the contract, the person named below shall act as Contractor’s Authorizing Person: ________________________________________

| Name: |  |
| --- | --- |
| In the capacity of: |  |
| Signed: |  |
| Duly authorized to sign the Bid for and on behalf of: |  |
| Date: |  |

  - Subcontractors Form

Please provide a list of qualified sub-contractors (if any) that will be deployed on the project:

| No. | Subcontractors | Scope |
| --- | --- | --- |

  - Project Engineer Form

Please give the name and, attach a copy of the Professional Registration Certificate of the person under whose authority the constructions shall be done.

  - Capacity Form

Number of Piping-technicians; Degree/Diploma Qualified staffs available for the project [names, years of experience]:

___________________________________________________________

Number of Electrical Technicians; Diploma available for the project [names, years of experience]:

___________________________________________________________

  - Draft Purchase Order

Attached in separate file.

  - Pricing the BOQs

Attached separately in excel sheets for each site