PURCHASE ORDER

| CHAI Reference: RFP/CHAI-TZ-EAPOA-002/25, Project ID: CHTANZCEM2 Grant ID: UNITAIDEM1 | Vendor’s Reference CHAI/EAPOA-003/26 |
| --- | --- |
| Description: The Clinton Health Access Initiative (CHAI) is supporting the strengthening of medical oxygen ecosystems, including the improvement of medical oxygen availability and supply systems in Eastern Africa through support of UNITAID. The East Africa Program on Oxygen Access (EAPOA) aims to improve access to medical oxygen in low- and middle-income countries (LMICs) across East Africa. The initiative seeks to bolster the capacity of local manufacturers to meet the growing demand for medical oxygen. The Proposed Project for Installation, Testing and Commissioning of Medical Oxygen VIE-Tanks, Control Panel, and Vaporizers to ten (10) Hospital-sites in different regions that include Bochi-Hospital - Dar Es Salaam, Tumbi Regional Referral Hospital - Coast, Morogoro Regional Referral Hospital - Morogoro, Sekou Toure Regional Referral Hospital - Mwanza, Mbeya Regional Referral Hospital - Mbeya, Songea Regional Referral Hospital - Ruvuma, Saint Benedict Ndanda Referral Hospital - Mtwara, Dodoma Regional Referral Hospital - Dodoma, Manyara Regional Referral Hospital - Manyara and, Mount Meru Regional Referral Hospital - Arusha |  |
| Purchaser Information: CHAI Program: Essential Medicine Program. Country: Tanzania Address: P.O Box 77277 Dar Es Salaam, Tanzania. Tel: +255-22-21219945 Fax: Headquarters Address: 383 Dorchester Avenue, Suite 400 Boston, MA 02127 USA | Supplier Information: ________________________ Address: P.O. Box _____________________________ Tel: +255 _____________________ Fax: ____________________________ |
| Contact: Dr. Esther Mtumbuka Title: Country Director, CHAI-Tanzania Email: emtumbuka@clintonHealthAccess.org | Contact: __________________________ Title: _____________________________ Email: _____________________________ Website: _____________________________ |
| Consignee Details: |  |
| Are the goods being delivered by Supplier or picked up by CHAI? | Delivered by Supplier to relevant project sites for Installations in Mainland Tanzania |
| Applicable INCOTERMS: | Delivery at Place unloaded (DPU) Incoterms 2020 |
| Delivery Location(s): | i)Sekou Toure Regional Referral Hospital - Mwanza, ii)Mbeya Regional Referral Hospital - Mbeya, iii)Songea Regional Referral Hospital - Ruvuma, iv)Dodoma Regional Referral Hospital – Dodoma and, v)Manyara Regional Referral Hospital - Manyara |
| Delivery Date: | Project delivery within ____ (___) days including installation, testing, commissioning and handing over. |
| Payment Schedule: | See 6. Payment Terms at Contract Amount of Shillings ___________ only (_________) VAT-exclusive |
| Enclosures: | - Goods - Purchase Order Terms and Conditions - ANNEX A: 1-Consignee details and required shipping documents - ANNEX B: 1- Supply and installation requirement, 2-Specifications of automatic oxygen change over panel and pipeline system, 3- Flowmeter specification, 4 - Humidifier Specification - APPENDIX 1: Drawings - APPENDIX 2: Matrix of Issues Negotiated |

GOODS

| Item | Healthcare Facility | AMOUNT-VAT-EXC | VAT | AMOUNT WITH VAT |
| --- | --- | --- | --- | --- |
| 1 | Mbeya Regional Referral Hospital |  |  |  |
| 2 | Morogoro Regional Referral Hospital |  |  |  |
| 3 | Songea Regional Referral Hospital |  |  |  |
| 4 | Manyara Regional Referral Hospital |  |  |  |
| 5 | Dodoma Regional Referral Hospital |  |  |  |
|  | GRAND TOTAL |  |  |  |

|  | VIE TANK INSTALLATION |  |  | MBEYA RRH |  |
| --- | --- | --- | --- | --- | --- |
|  | REFERENCE NUMBER | RFP/CHAI-TZ-EAPOA-002/25 |  |  |  |
| No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT |
| 1.0 | Piping (Copper pipe manufactured from phosphorus de-oxidized non-arsenical copper to conform to BS EN HTM02-01) |  |  |  |  |
|  | 22mm diameter degreased copper pipes in metres | 58 | LM |  |  |
| 2.0 | Piping Accessories Straight Couplers: |  |  |  |  |
|  | 22mm diameter degreased copper straight couplers | 30 | Pcs |  |  |
| 3.0 | Elbows: |  |  |  |  |
|  | 22mm diameter degreased copper elbows | 30 | Pcs |  |  |
| 4.0 | Reducers: |  |  |  |  |
|  | 28x22mm diameter degreased copper reducer | 2 | Pcs |  |  |
|  | 22x15mm diameter degreased copper reducer | 4 | Pcs |  |  |
| 5.0 | Line ball valves c/w NIST (Medical gas line valves conforming to HTM 02-01) |  |  |  |  |
|  | 22mm medical gas line valves | 1 | Item |  |  |
|  | 15mm medical gas line valves | 1 | Item |  |  |
|  | 22mm medical gas line Non Return valves | 2 | Item |  |  |
|  | 15mm medical gas line Non Return valves | 2 | Item |  |  |
|  | Total carried to collection on page 2 |  |  |  |  |
|  | Page 1 of 2 |  |  |  |  |
|  | REFERENCE NUMBER |  |  |  |  |
| No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT |
| 6.0 | Mounting accessories |  |  |  |  |
|  | 22mm munsen rings complete with clamps | 30 | Item |  |  |
|  | M10 threaded rod | 3 | LM |  |  |
|  | M10 hungers | 60 | no |  |  |
| 7.0 | Lifting & Cranage , Tansportation and Installation of the Liquid Oxygen VIE Tank ,10,000 Litres Capacity (Empty Weight - 5 Tons-Diameter-2.5m-Height- 6m) | 1 | Sum |  |  |
| 8.0 | Any Other Item necessary for Inter connecting the VIE Tank, the Vaporizer,the Reducing station and the existing(Specify) piping | 1 | Sum |  |  |
| 9.0 | Power Provision Single Phase, Twin Socket 240V, 50Hz( Cable size 6 mm2) | 50 | LM |  |  |
| 10.00 | Labour Cost (Installation, Testing & Commissioning) | 1 | Item |  |  |
| 11.00 | Provision of at least 2 appropriate Fire Extinguishers (Carbon Dioxide or Dry Chemical type) to be placed/anchored nearby the VIE system | 1 | Sum |  |  |
| 12 | VIE Tank Earthing | 1 | Item |  |  |
|  | Total carried to collection below |  |  |  |  |
|  | Collection: |  |  |  |  |
|  | Total brought forward from page 1 |  |  |  |  |
|  | Total brought down from above |  |  |  |  |
|  | Total |  |  |  |  |
|  | Add 18% VAT |  |  |  |  |
|  | Grand Total |  |  |  |  |

|  | VIE TANK INSTALLATION |  |  | MOROGORO RRH |  |
| --- | --- | --- | --- | --- | --- |
|  | REFERENCE NUMBER | RFP/CHAI-TZ-EAPOA-002/25 |  |  |  |
| No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT |
| 1.0 | Piping (Copper pipe manufactured from phosphorus de-oxidized non-arsenical copper to conform to BS EN HTM02-01) |  |  |  |  |
|  | 22mm diameter degreased copper pipes in metres | 58 | LM |  |  |
| 2.0 | Piping Accessories Straight Couplers: |  |  |  |  |
|  | 22mm diameter degreased copper straight couplers | 30 | Pcs |  |  |
| 3.0 | Elbows: |  |  |  |  |
|  | 22mm diameter degreased copper elbows | 30 | Pcs |  |  |
| 4.0 | Reducers: |  |  |  |  |
|  | 28x22mm diameter degreased copper reducer | 2 | Pcs |  |  |
|  | 22x15mm diameter degreased copper reducer | 4 | Pcs |  |  |
| 5.0 | Line ball valves c/w NIST (Medical gas line valves conforming to HTM 02-01) |  |  |  |  |
|  | 22mm medical gas line valves | 1 | Item |  |  |
|  | 15mm medical gas line valves | 1 | Item |  |  |
|  | 22mm medical gas line Non Return valves | 2 | Item |  |  |
|  | 15mm medical gas line Non Return valves | 2 | Item |  |  |
|  | Total carried to collection on page 2 |  |  |  |  |
|  | Page 1 of 2 |  |  |  |  |
|  | REFERENCE NUMBER |  |  |  |  |
| No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT |
| 6.0 | Mounting accessories |  |  |  |  |
|  | 22mm munsen rings complete with clamps | 30 | Item |  |  |
|  | M10 threaded rod | 3 | LM |  |  |
|  | M10 hungers | 60 | no |  |  |
| 7.0 | Lifting & Cranage , Tansportation and Installation of the Liquid Oxygen VIE Tank ,6000 Litres Capacity (Empty Weight - 5 Tons-Diameter-2.5m-Height- 6m) | 1 | Sum |  |  |
| 8.0 | Any Other Item necessary for Inter connecting the VIE Tank, the Vaporizer,the Reducing station and the existing(Specify) piping | 1 | Sum |  |  |
| 9.0 | Power Provision Single Phase, Twin Socket 240V, 50Hz( Cable size 6 mm2) | 40 | LM |  |  |
| 10.00 | Labour Cost (Installation, Testing & Commissioning) | 1 | Item |  |  |
| 11.00 | Provision of at least 2 appropriate Fire Extinguishers (Carbon Dioxide or Dry Chemical type) to be placed/anchored nearby the VIE system | 1 | Sum |  |  |
| 12 | VIE Tank Earthing | 1 | Item |  |  |
|  | Total carried to collection below |  |  |  |  |
|  | Collection: |  |  |  |  |
|  | Total brought forward from page 1 |  |  |  |  |
|  | Total brought down from above |  |  |  |  |
|  | Total |  |  |  |  |
|  | Add 18% VAT |  |  |  |  |
|  | Grand Total |  |  |  |  |

|  | VIE TANK INSTALLATION | SONGEA RRH |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | REFERENCE NUMBER | RFP/CHAI-TZ-EAPOA-002/25 |  |  |  |
| No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT |
| 1.0 | Piping (Copper pipe manufactured from phosphorus de-oxidized non-arsenical copper to conform to BS EN HTM02-01) |  |  |  |  |
|  | 22mm diameter degreased copper pipes in metres | 58 | LM |  |  |
| 2.0 | Piping Accessories Straight Couplers: |  |  |  |  |
|  | 22mm diameter degreased copper straight couplers | 30 | Pcs |  |  |
| 3.0 | Elbows: |  |  |  |  |
|  | 22mm diameter degreased copper elbows | 30 | Pcs |  |  |
| 4.0 | Reducers: |  |  |  |  |
|  | 28x22mm diameter degreased copper reducer | 2 | Pcs |  |  |
|  | 22x15mm diameter degreased copper reducer | 4 | Pcs |  |  |
| 5.0 | Line ball valves c/w NIST (Medical gas line valves conforming to HTM 02-01) |  |  |  |  |
|  | 22mm medical gas line valves | 1 | Item |  |  |
|  | 15mm medical gas line valves | 1 | Item |  |  |
|  | 22mm medical gas line Non Return valves | 2 | Item |  |  |
|  | 15mm medical gas line Non Return valves | 2 | Item |  |  |
|  | Total carried to collection on page 2 |  |  |  |  |
|  | Page 1 of 2 |  |  |  |  |
|  | REFERENCE NUMBER |  |  |  |  |
| No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT |
| 6.0 | Mounting accessories |  |  |  |  |
|  | 22mm munsen rings complete with clamps | 30 | Item |  |  |
|  | M10 threaded rod | 3 | LM |  |  |
|  | M10 hungers | 60 | no |  |  |
| 7.0 | Lifting & Cranage , Tansportation and Installation of the Liquid Oxygen VIE Tank ,6000 Litres Capacity (Empty Weight - 5 Tons-Diameter-2.5m-Height- 6m) | 1 | Sum |  |  |
| 8.0 | Any Other Item necessary for Inter connecting the VIE Tank, the Vaporizer,the Reducing station and the existing(Specify) piping | 1 | Sum |  |  |
| 9.0 | Power Provision Single Phase, Twin Socket 240V, 50Hz( Cable size 6 mm2) | 30 | LM |  |  |
| 10.00 | Labour Cost (Installation, Testing & Commissioning) | 1 | Item |  |  |
| 11.00 | Provision of at least 2 appropriate Fire Extinguishers (Carbon Dioxide or Dry Chemical type) to be placed/anchored nearby the VIE system | 1 | Sum |  |  |
| 12 | VIE Tank Earthing | 1 | Item |  |  |
|  | Total carried to collection below |  |  |  |  |
|  | Collection: |  |  |  |  |
|  | Total brought forward from page 1 |  |  |  |  |
|  | Total brought down from above |  |  |  |  |
|  | Total |  |  |  |  |
|  | Add 18% VAT |  |  |  |  |
|  | Grand Total |  |  |  |  |

|  | VIE TANK INSTALLATION |  |  | MANYARA RRH |  |
| --- | --- | --- | --- | --- | --- |
|  | REFERENCE NUMBER | RFP/CHAI-TZ-EAPOA-002/25 |  |  |  |
| No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT |
| 1.0 | Piping (Copper pipe manufactured from phosphorus de-oxidized non-arsenical copper to conform to BS EN HTM02-01) |  |  |  |  |
|  | 22mm diameter degreased copper pipes in metres | 58 | LM |  |  |
| 2.0 | Piping Accessories Straight Couplers: |  |  |  |  |
|  | 22mm diameter degreased copper straight couplers | 30 | Pcs |  |  |
| 3.0 | Elbows: |  |  |  |  |
|  | 22mm diameter degreased copper elbows | 30 | Pcs |  |  |
| 4.0 | Reducers: |  |  |  |  |
|  | 28x22mm diameter degreased copper reducer | 2 | Pcs |  |  |
|  | 22x15mm diameter degreased copper reducer | 4 | Pcs |  |  |
| 5.0 | Line ball valves c/w NIST (Medical gas line valves conforming to HTM 02-01) |  |  |  |  |
|  | 22mm medical gas line valves | 1 | Item |  |  |
|  | 15mm medical gas line valves | 1 | Item |  |  |
|  | 22mm medical gas line Non Return valves | 2 | Item |  |  |
|  | 15mm medical gas line Non Return valves | 2 | Item |  |  |
|  | Total carried to collection on page 2 |  |  |  |  |
|  | Page 1 of 2 |  |  |  |  |
|  | REFERENCE NUMBER |  |  |  |  |
| No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT |
| 6.0 | Mounting accessories |  |  |  |  |
|  | 22mm munsen rings complete with clamps | 30 | Item |  |  |
|  | M10 threaded rod | 3 | LM |  |  |
|  | M10 hungers | 60 | no |  |  |
| 7.0 | Lifting & Cranage , Tansportation and Installation of the Liquid Oxygen VIE Tank ,6000 Litres Capacity (Empty Weight - 5 Tons-Diameter-2.5m-Height- 6m) | 1 | Sum |  |  |
| 8.0 | Any Other Item necessary for Inter connecting the VIE Tank, the Vaporizer,the Reducing station and the existing(Specify) piping | 1 | Sum |  |  |
| 9.0 | Power Provision Single Phase, Twin Socket 240V, 50Hz( Cable size 6 mm2) | 40 | LM |  |  |
| 10.00 | Labour Cost (Installation, Testing & Commissioning) | 1 | Item |  |  |
| 11.00 | Provision of at least 2 appropriate Fire Extinguishers (Carbon Dioxide or Dry Chemical type) to be placed/anchored nearby the VIE system | 1 | Sum |  |  |
| 12 | VIE Tank Earthing | 1 | Item |  |  |
|  | Total carried to collection below |  |  |  |  |
|  | Collection: |  |  |  |  |
|  | Total brought forward from page 1 |  |  |  |  |
|  | Total brought down from above |  |  |  |  |
|  | Total |  |  |  |  |
|  | Add 18% VAT |  |  |  |  |
|  | Grand Total |  |  |  |  |

|  | VIE TANK INSTALLATION |  |  | DODOMA RRH |  |
| --- | --- | --- | --- | --- | --- |
|  | REFERENCE NUMBER | RFP/CHAI-TZ-EAPOA-002/25 |  |  |  |
| No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT |
| 1.0 | Piping (Copper pipe manufactured from phosphorus de-oxidized non-arsenical copper to conform to BS EN HTM02-01) |  |  |  |  |
|  | 22mm diameter degreased copper pipes in metres | 145 | LM |  |  |
| 2.0 | Piping Accessories Straight Couplers: |  |  |  |  |
|  | 22mm diameter degreased copper straight couplers | 60 | Pcs |  |  |
| 3.0 | Elbows: |  |  |  |  |
|  | 22mm diameter degreased copper elbows | 60 | Pcs |  |  |
| 4.0 | Reducers: |  |  |  |  |
|  | 28x22mm diameter degreased copper reducer | 2 | Pcs |  |  |
|  | 22x15mm diameter degreased copper reducer | 4 | Pcs |  |  |
| 5.0 | Line ball valves c/w NIST (Medical gas line valves conforming to HTM 02-01) |  |  |  |  |
|  | 22mm medical gas line valves | 1 | Item |  |  |
|  | 15mm medical gas line valves | 1 | Item |  |  |
|  | 22mm medical gas line Non Return valves | 2 | Item |  |  |
|  | 15mm medical gas line Non Return valves | 2 | Item |  |  |
|  | Total carried to collection on page 2 |  |  |  |  |
|  | Page 1 of 2 |  |  |  |  |
|  | REFERENCE NUMBER |  |  |  |  |
| No. | DESCRIPTION | QTY | UNIT | RATE | AMOUNT |
| 6.0 | Mounting accessories |  |  |  |  |
|  | 22mm munsen rings complete with clamps | 30 | Item |  |  |
|  | M10 threaded rod | 3 | LM |  |  |
|  | M10 hungers | 90 | no |  |  |
| 7.0 | Lifting & Cranage , Tansportation and Installation of the Liquid Oxygen VIE Tank ,6000 Litres Capacity (Empty Weight - 5 Tons-Diameter-2.5m-Height- 6m) | 1 | Sum |  |  |
| 8.0 | Any Other Item necessary for Inter connecting the VIE Tank, the Vaporizer,the Reducing station and the existing(Specify) piping | 1 | Sum |  |  |
| 9.0 | Power Provision Single Phase, Twin Socket 240V, 50Hz( Cable size 6 mm2) | 30 | LM |  |  |
| 10.00 | Labour Cost (Installation, Testing & Commissioning) | 1 | Item |  |  |
| 11.00 | Provision of at least 2 appropriate Fire Extinguishers (Carbon Dioxide or Dry Chemical type) to be placed/anchored nearby the VIE system | 1 | Sum |  |  |
| 12 | VIE Tank Earthing | 1 | Item |  |  |
|  | Total carried to collection below |  |  |  |  |
|  | Collection: |  |  |  |  |
|  | Total brought forward from page 1 |  |  |  |  |
|  | Total brought down from above |  |  |  |  |
|  | Total |  |  |  |  |
|  | Add 18% VAT |  |  |  |  |
|  | Grand Total |  |  |  |  |

VENDOR DOSSIER

The vendor dossier for VIE-Tank and MGPS installation, pipeline materials and design contains the following supplier-provided information:

- Technical Information: Device/equipment classification and name shall be accompanied by technical information in English, such as leaflets, brochures, or catalogue pages, in line with requisite technical specifications.

- Proof of Quality: The installation of a MGPS, including manifold systems, should only be carried out by specialist firms certified in ISO 9001 or ISO 13485, with a clearly specified scope of registration for these activities. Additionally, device-specific product performance standards (all products) and/or Stringent Regulatory Authority approval/marking for applicable devices must be met—see Annex B (1 to 6) for details, with 5 and 6 specifically containing design drawings. All pipe networks must be purged, inspected, tested, and commissioned for medical oxygen service according to ISO 7396-1.

- Warranties: Warranty for devices, installation, and warranty on labour, including information on how any issues are managed should they arise under the warranty period. Warranties should be managed directly via the consignee of each product, (i.e., country governments). Warranty period is for 2 years.

- Collaborations; the Vendor for Installations shall collaborate with the VIE-Tanks-Supplier in the following key-areas: -

- Ready to work with the VIE-Tanks-Supplier in case of weaknesses or defects;

- Proper procedures for replacement of defective VIE-Tank or pipes;

- Critical requirements/guidelines prior-to-installations;

- Third-party inspections by Tanzania Medical and Drugs Authority (TMDA) or any other authorized institution after installations on site are mandatory;

- Conducting joint-user-trainings;

- Product Recall: The Supplier is responsible for notifying the consignee and issuing an advisory notice in the event that a product must be recalled; the Supplier will be responsible for communicating, conducting, and paying for any involuntary product recalls.

THE ATTACHED TERMS AND CONDITIONS ARE INCORPORATED HEREIN, AND TOGETHER WITH THE PURCHASE ORDER FORM THE ENTIRE AGREEMENT BETWEEN THE PARTIES WHICH HAS BEEN DULY AUTHORIZED BY ALL NECESSARY CORPORATE OR COMPANY ACTION AND HAS BEEN EXECUTED AND DELIVERED BY AN AUTHORIZED REPRESENTATIVE OF EACH PARTY. ANY ADDITIONAL OR CONFLICTING TERMS TO THE PURCHASE ORDER OR THE TERMS IS HEREBY REJECTED UNLESS AGREED TO BY THE PARTIES IN WRITING.

| CHAI Signature: | VENDOR’S Signature: / |
| --- | --- |
| Name: Esther Mtumbuka | Name: ___________________________ |
| Title: Country Director, Tanzania | Title: ____________________________ |
| Date: ___________________________ 2026 | Date: ________________________ 2026 |

PURCHASE ORDER
Terms and Conditions

- Applicability

  - These terms and conditions apply to the purchase order (the “Purchase Order”) attached hereto, and is an offer by Clinton Health Access Initiative, Inc. (“CHAI”) for the purchase of the goods specified on the Purchase Order (the “Goods”) from the party named as a supplier on the Purchase Order (the “Supplier”) in accordance with and subject to these terms and conditions (the “Terms”; together with the Purchase Order, this “Order”). This Order, together with any documents incorporated herein by reference, constitutes the sole and entire agreement of the parties with respect to the Order, and supersedes all prior or contemporaneous understandings, agreements, negotiations, representations and warranties, and communications, both written and oral, with respect to the subject matter of the Order. These Terms prevail over any terms or conditions contained in any other documentation and expressly exclude and supersede any of Supplier’s general terms and conditions of sale or any other document issued or presented by Supplier in connection with this Order.

  - These Terms apply to any repaired or replacement Goods provided by Supplier hereunder.

  - CHAI is not obligated to any minimum purchase or future purchases under this Order.

- Acknowledgement Copy

Supplier’s execution of the Purchase Order or commencement of performance under this Order, or acceptance of any payment from CHAI, shall constitute acceptance by Supplier of this Order subject to these Terms.

- Delivery / Pick-Up Terms

  - Goods shall be delivered or made available for pickup at the location and date specified on the Purchase Order _________ 2026. Supplier shall bear all risk of loss to Goods until CHAI submits written acknowledgement of receipt of Goods.

  - Supplier commits to submitting an invoice and itemized packing list of the Goods provided to CHAI either before or by the Delivery Date.

  - CHAI shall be responsible for arranging all required customs clearances unless otherwise agreed in writing by the parties hereto.  No pass-through charges will be permitted for packing, crating, freight, local cartage, customs duties and/or any other such service not specified in the Purchase Order.

  - Time is of the essence and failure to deliver in accordance with the delivery schedule under this Order shall be considered a material breach of this Order. Supplier shall notify CHAI immediately of any actual or potential delay.

# Installation, Training, Handover

- The vendor will perform staging of works, installation, testing, and commissioning of Medical Gas Pipelines should be carried out as per ISO 7396-1 and HTM 02-01.

- Pipeline installation shall be carried out according to the drawings provided in Annexes 5 and 6, ensuring utmost cleanliness suitable for medical oxygen use.

- Copper piping shall be deoxidized, degreased, and shall be sold and delivered capped at both ends to minimize contamination prior to installation.

- Documentation of cleaning and degreasing as per BS EN 13348 shall be provided to CHAI prior to installation.

- The procurement of piping materials and components as well as system design and installation for medicinal oxygen piped networks shall all be based on design guidance HTM 02-01. System design and installation shall be carried out only by certified individuals. All pipe networks to be purged, inspected, and tested and commissioned for medical oxygen service according to HTM 02-01.

- Manufacturer’s test certificates for both chemical composition and physical properties shall be provided prior to installation.

- Pipes shall be clearly labeled with manufacturer’s name or registered trademark, product type, specification, and traceable batch number or production date (note, must indicate suitable for medical oxygen service).

- Fittings shall be brought in sealed individual packages. Pipe fixing clamps shall be of non-ferrous and non-deteriorating plastic suitable for the diameter of the pipe. All pipe clamps shall be non-reactive to copper.

- Adequate support shall be provided while laying pipelines to ensure that the pipes do not sag. The spacing for supports as per the bid document specification for any size of pipe. Suitable sleeves shall be provided wherever pipes cross through walls/slabs.

- The system shall be tested according to ISO7396-1 and HTM 02-01. All the piping system should be tested in the presence of the client engineer or his authorized representative. All leaks and joints revealed during testing should be rectified and re-tested till the pressure in pipes stands for at least 24 hours.

- Comprehensive training shall be delivered to hospital staff prior to handover, including topics such as safe handling of medical gases and discharge cylinder pressure, management of connections and connections in cases of emergency, and leak detection methods.

- Device/equipment classification and name shall be accompanied by technical information in English, such as leaflets, brochures, or catalog pages, in line with requisite technical specifications.

- A commissioning report and certificate should be delivered upon completion of activities. If the final installation deviates from the proposed drawings (Annexed), the vendor shall supply the facility with as-built drawings for the sake of appropriate record keeping.

- The Supplier shall notify CHAI and the consignee by issuing an advisory notice in the event that a product must be recalled; the Supplier will be responsible for communicating, conducting, and paying for any involuntary product recalls.

- Quantity

If Supplier delivers more or less than ten percent (10%) of the quantity of Goods ordered, CHAI may reject at its sole discretion all or any excess Goods. Any such rejected Goods shall be returned to Supplier at Supplier’s sole risk and expense. If CHAI does not reject the Goods and instead accepts the delivery of Goods at the increased or reduced quantity, the amount owed for the extra Goods shall be adjusted on a pro-data basis.

- Payment Terms

- Payment schedule

- No advance payment;

- Verification by CHAI, and Experts-Team’s inspection cum-certification, verification, sign off and submission of an invoice by the supplier is a must;

- Payment within 21-days will be done proportion to the work-done against the scope-of-works (Bills of Quantities) but the physical-performance in each claim must be more than 25% from the previous claim;

- Last but one claim at practical completion must will involve testing, commissioning, TMDA-certifications and project handover to CHAI and MOH;

- A 7.5% retention amount shall be paid within 21 days after the 1st Year of warranty upon MoH and/or Experts-Team’s confirmation and submission of invoice by the supplier;

- A 2.5% retention shall be paid within 21 days after the 2nd and final year of warranty upon MOH and/or Experts-Team’s confirmation and submission of invoice by the supplier;

- Each invoice shall specify bank wiring instructions or delivery instructions for cash transfers to take place. Payment will be made in Tanzanian shillings. If CHAI fails or delay to pay pre-payment, Supplier has the right to postpone the delivery to account for actual number of days delays occurred.

- Payment for Goods/works pursuant to the Order shall not be deemed an acceptance of the Goods/works

- Payment certification

    - The Experts-Team shall inspect, verify and certify compliance of the installation work completed to the requirements of this purchase order.

    - Experts-Team shall issue a Payment Certificate within Seven (7) days of the Supplier's request for payment, provided that the work is verified and deemed satisfactory.

    - Each request for payment must be accompanied by detailed documentation of the progress, including photographs, installation reports, as applicable.

    - Payment for Goods/works pursuant to the Order shall not be deemed an acceptance of the Goods.

    - Adjustments shall be made to scheduled payments in the event of incomplete or non-compliant work as identified during the certification process. Deductions will correspond to the value of the uncompleted or unsatisfactory work until such deficiencies are rectified to the satisfaction of Experts-Team and in accordance with the contractual specifications.

    - If the Supplier disputes the accuracy or fairness of a Payment Certificate issued by Experts-Team, the Supplier is required to formally notify Experts-Team and CHAI in writing within seven (7) days of receiving the certificate. The notification should detail the reasons for the disagreement. The Supplier, Experts-Team, and CHAI shall then engage in good faith consultation to resolve the issue amicably within fourteen (14) days of such notification.

    - Should the consultation under the previous clauses fail to resolve the dispute to the satisfaction of all parties involved, the Supplier may escalate the matter according to the Dispute Resolution procedures specified in the Governing Law and Dispute section of this contract.

- Price

The total amount due for the Goods is the total price listed on the Purchase Order (the “Price”). Unless otherwise specified in the Order, the Price includes all applicable fees including, but not limited to packaging, transportation costs, insurance, customs duties and fees and applicable taxes, all, harmonized sales tax, goods and services tax, value added tax, use or excise taxes. No increase in the Price is effective, whether due to increased material, labor or transportation costs or otherwise, without the prior written consent of CHAI. Supplier shall be responsible for, and shall pay directly, any and all corporate and personal income taxes imposed on Supplier and its employees by the legislation of the country of incorporation of Supplier and/or performance of the work and related to the execution of the Order.

- Liquidated Damages

If the supplier fails to complete the agreed delivery within the time or times specified in this purchase order agreement, CHAI at its option may, solely or through CHAI’s appointed debt recovery agent at the time, recover from the supplier as a debt or deduct from any payment owed to the supplier one percent (1%) of this purchase order’s grand total value for the project and/or deliverables being delayed per day by way of liquidated damages and up to a maximum of 30 days after which the contract will be terminated. CHAI at its option will make informed decision(s) to impose or waive the recovery of liquidated damages taking into account on time project completion, disruptive circumstances beyond suppliers control, acceptable justification for delays, proactive measures to mitigate and resolve delays, supplier’s demonstrated commitment to project success, quality project delivery, transparent and proactive communications by the supplier and/or consistent compliance to contractual obligations.

# Reporting Requirements. Supplier shall furnish to the CHAI Tanzania Oxygen – work Program

Manager with the A&E firm in copy.

Supplier shall furnish updated work-plan to the CHAI and Expert-Team.

| Report Type | Reporting period | Submission Deadline |
| --- | --- | --- |
| Updated Program of works/Work plan | As may be needed | Within 7 days after contract signing |
| Project Progress Report | Weekly | Thursday Morning/ 10:00AM |

- Late-submission of updated work program and weekly-report as from the date of signing the addendum shall be penalized at 1% of the Contract Sum for a maximum period of 30-days and beyond that it is breach of contract for determination.

- Alteration of agreed work plan without prior approval by CHAI shall constitute to breach of contract for determination.

- Each Report must follow the template to be provided by CHAI. Partner shall also include in any report to CHAI such other information that CHAI may request during a Reporting Period including any related documentation.

- Shipping Terms

  - Delivery shall be made in accordance with Incoterms® 2020, along with the terms specified on the face of this Order. Supplier shall provide written notice of shipment to CHAI when the Goods are delivered to a carrier for transportation. Supplier shall provide CHAI all shipping documents, including the commercial invoice, packing list, air waybill and bill of lading, and any other documents necessary to release the Goods to CHAI after Supplier delivers the Goods to the transportation carrier (“Shipping Documents”). The Order number must appear on all Shipping Documents and any other documents pertaining to the Order. In the event of any conflict between Incoterms® 2020 and these terms and conditions, these terms and conditions shall govern.

  - All Goods shall be packed for shipment according to CHAI’s instructions or, if there are no instructions, in a manner sufficient to ensure that the Goods are delivered in undamaged condition and in accordance with applicable law and industry standards. Supplier shall provide CHAI with shipment documentation showing the Supplier Reference Number, the quantity of pieces in the shipment, the number of cartons or containers in the shipment, Supplier’s name, the bill of lading number and the country of origin. Supplier must provide CHAI prior written notice if it requires CHAI to return any packaging material. Any return of such packaging material shall be made at Supplier’s sole cost and expense.

- Warranties

Supplier warrants to CHAI that all Goods will:

  - be free from any defects in workmanship, material and design;

  - conform to applicable specifications, drawings, designs, samples and other requirements specified by CHAI;

  - comply with all applicable laws, regulations and ordinances;

  - meet the specifications and standards as approved by  Tanzania medicine and drug authority (TMDA), Tanzania Bureau of Standards (TBS) and any other relevant authorities as per country laws and regulations;

  - be fit for their intended purpose and operate as intended;

  - be merchantable;

  - be insured for their full value while being shipped or otherwise transported to CHAI;

  - be free and clear of all liens, security interests or other encumbrances; and

  - not infringe or misappropriate any third party’s patent or other intellectual property rights.

  - No substitutions, regarding the brand name, manufacturing site or item number, will be made without advance, written approval from CHAI quality.

  - CHAI can reject shipment if the product delivered doesn’t comply with the manufacturer and item number specified.

These warranties survive any delivery, inspection, acceptance or payment of or for the Goods by CHAI. These warranties are cumulative and in addition to any other warranty provided by law or equity. Any applicable statute of limitations runs from the date of CHAI’s discovery of the non-compliance of the Goods with the foregoing warranties. If CHAI gives Supplier notice of non-compliance of its obligations under this Section, or in the event of a recall of Goods by Supplier or applicable government agency, Supplier shall, at its sole cost and expense, promptly replace the defective or non-conforming Goods and pay for all related expenses, including, but not limited to, transportation charges for the return of the defective or non-conforming goods to Supplier and the delivery of replacement Goods to CHAI.

- Inspection and Rejection of Non-Conforming Goods

CHAI has the right to inspect the Goods on or after the Delivery Date. CHAI, at its sole option, may inspect all or a sample of the Goods, and may reject all or any portion of the Goods if it determines the Goods are non-conforming or defective. CHAI may contract an independent third party to perform quality control testing. If CHAI rejects any portion of the Goods, CHAI has the right, effective upon written notice to Supplier, to: (a) rescind the Order in its entirety; (b) accept the Goods at a reasonably reduced price; or (c) reject the Goods and require replacement of the rejected Goods. If CHAI requires replacement of the Goods, Supplier shall, at its sole expense, within thirty (30) days replace the non-conforming Goods and pay for all related charges, including, but not limited to, transportation charges for the return of the defective goods and the delivery of replacement Goods. If Supplier fails to timely deliver replacement Goods, CHAI may replace them with goods from a third party and charge Supplier the cost thereof and terminate this Order for cause pursuant to Section 19. Any inspection or other action by CHAI under this Section shall not reduce or otherwise affect Supplier’s obligations under the Order, and CHAI shall have the right to conduct further inspections after Supplier has carried out its remedial actions.

- Most Favored Nation

Supplier represents and warrants that the price for Goods is the lowest price charged by Supplier to any of its external buyers for similar volumes of similar Goods. If Supplier charges any other buyer a lower price, Supplier must automatically apply the lower price to all Goods under this Order. If Supplier fails to apply the lower price, CHAI, at its option, may terminate this Order without liability pursuant to Section 19.

- Set-off

Without prejudice to any other right or remedy it may have, CHAI reserves the right to set off at any time any amount owed to it by Supplier against any amount payable by CHAI to Supplier.

- Assignment

Supplier shall not assign, transfer, delegate or subcontract any of its rights or obligations under the Order without the prior written consent of CHAI. Any purported assignment or delegation in violation of this Section shall be null and void. No assignment or delegation shall relieve the Supplier of any of its obligations hereunder. CHAI may at any time assign, transfer or subcontract any or all of its rights or obligations under the Order without Supplier’s prior written consent to any affiliate or to any person acquiring all or substantially all of CHAI’s assets.

- Use of Name, Emblem or Official Seal

This Order shall not be construed to grant Supplier any license to use CHAI’s name or logo whether now existing, or adapted in the future, in any format (the “CHAI Marks”).  Any requests for use of CHAI Marks shall be submitted in writing to CHAI.  CHAI shall have the right, in its sole discretion, to determine whether or not to grant any rights of usage to the CHAI Marks to Supplier.  In order for an authorization to be valid, it must be documented in writing from an authorized CHAI representative.

- No Third-Party Beneficiaries

This Order is for the sole benefit of the parties hereto and their respective successors and permitted assigns, and nothing herein, express or implied, is intended to or shall confer upon any other person or entity any legal or equitable right, benefit or remedy of any nature whatsoever under or by reason of these Terms.

- No Agency

The parties are independent entities and the employees of one party shall not be deemed employees, agents, partners, joint venturers or representatives of the other. Neither party has the power or authority to act for, represent or bind the other. CHAI shall not be responsible for any act or omission of Supplier, its employees, contractors or agents. Supplier’s personnel described in this Order are not employees of CHAI and are neither eligible for CHAI employee benefits nor covered under CHAI’s insurance policies. Supplier is solely responsible for its employees’ supervision, daily direction and control, and payment of salary (including, without limitation, withholding of income taxes and social security), workers’ compensation and disability benefit.

- Insurance

During the term of the Order, Supplier shall, at its own expense, procure and maintain all required insurance in full force and effect which includes, but is not limited to comprehensive general liability, product liability, workers’ compensation and damage insurance with financially sound and reputable insurers. Upon CHAI’s request, Supplier shall provide CHAI with a certificate of insurance from Supplier’s insurer evidencing the insurance coverage specified in this Order. Supplier shall provide CHAI with thirty (30) days’ advance written notice in the event of a cancellation or material change in Supplier’s insurance policy. Except where prohibited by law, Supplier shall require its insurer to waive all rights of subrogation against CHAI’s insurers and CHAI.

- Compliance with Law

Supplier is in compliance with and shall comply with all applicable laws, regulations and ordinances. Supplier has and shall maintain in effect all the licenses, permissions, authorizations, consents and permits that it needs to carry out its obligations under the Order. Supplier shall comply with all export and import laws of all countries involved in the sale of Goods under this Order. Supplier assumes all responsibility for shipments of Goods requiring any government import clearance. CHAI may terminate this Order if any government authority imposes antidumping duties, countervailing duties or any retaliatory duties or any other penalties on the Goods.

- Governing Law and Disputes

## The validity and interpretation of the agreement between CHAI and the Supplier shall be governed by the laws of the United Republic of Tanzania, but without reference to the principles of choice of law. The application of the United Nations Convention on Contracts for the International Sales of Goods (1980) is excluded.

- Termination

CHAI may terminate this Order, in whole or in part, at any time with or without cause for undelivered Goods on ten (10) days’ prior written notice to Supplier. In addition to any remedies that may be provided under these Terms, CHAI may terminate this Order with immediate effect upon written notice to the Supplier, either before or after the acceptance of the Goods, if Supplier has not performed or complied with any of these Terms, in whole or in part. If the Supplier becomes insolvent, is generally unable to pay, or fails to pay, its debts as they become due, files a petition for bankruptcy or commences or has commenced against it proceedings relating to bankruptcy, receivership, reorganization, arrangement or assignment for the benefit of creditors, then CHAI may terminate this Order upon written notice to Supplier. If CHAI terminates the Order for any reason, Supplier’s sole and exclusive remedy is payment for the Goods received and accepted by CHAI prior to the termination.

- Modification

None of the terms and conditions contained in this Order may be added to, modified, superseded or otherwise altered except by a written instrument signed by an authorized representative of CHAI and Supplier.

- Indemnification

Supplier further agrees to and hereby does indemnify, defend and hold harmless CHAI, its directors, officers and employees from any and all claims, judgments, costs, liabilities, damages and expenses whatsoever, including reasonable attorneys’ fees, arising from any acts or omissions in the provision by Supplier of its obligations under this Order. This provision shall survive termination or expiration of this Agreement.

- Limitation of Liability

Nothing in this Order shall exclude or limit Supplier’s liability under the Order.  CHAI’s liability under this order shall be limited to the total amount paid under this Order.

- Confidential Information

In connection with the Order, Supplier and CHAI (as to information disclosed, the “Disclosing Party”) may each provide the other party (as to information received, the “Receiving Party”) with Confidential Information. “Confidential Information” means (a) all pricing information, financial information, business information or intellectual property, (b) all Terms, (c) all information that is designated in writing as “confidential” or “proprietary” by Disclosing Party at the time of written disclosure, and (d) all information that is orally designated as “confidential” or “proprietary” by Disclosing Party at the time of oral disclosure and is confirmed to be “confidential” or “proprietary” in writing within ten (10) days after oral disclosure.  The obligations of this Section shall not apply as to any portion of the Confidential Information that: (i) is or becomes generally available to the public other than from disclosure by Receiving Party, its representatives or its affiliates; (ii) is or becomes available to Receiving Party or its representatives or affiliates on a non-confidential basis from a source other than Disclosing Party when the source is not, to the best of Receiving Party’s knowledge, subject to a confidentiality obligation to Disclosing Party; (iii) is independently developed by Receiving Party, its representatives or affiliates, without use of the Confidential Information; (iv) is required to be disclosed by law, a valid legal process or a government agency; (v) is approved for disclosure in writing by an authorized representative of Disclosing Party or (vi) CHAI discloses to its financial advisors for analytical purposes. If Receiving Party or any of its affiliates or representatives is required by law, legal process or a government agency to disclose any Confidential Information, that party agrees to provide Disclosing Party with prompt written notice to permit Disclosing Party to seek an appropriate protective order or agency decision or to waive compliance by Receiving Party with the provisions of this Section.  In the event that efforts to secure confidential treatment are unsuccessful, Receiving Party may lawfully revise the Confidential Information to make it non-proprietary or to minimize the loss of its proprietary value.  Nothing in this Order grants Receiving Party any license to any invention, patent, trademark or copyright now or later owned or controlled by Disclosing Party.

- Force Majeure

No party shall be liable or responsible to the other party, nor be deemed to have defaulted under or breached this Order, for any failure or delay in fulfilling or performing any term of this Order (except for any obligations to make payments to the other party hereunder), when and to the extent such party’s (“Impacted Party”) failure or delay is caused by or results from the following force majeure events (“Force Majeure Event(s)”): (a) acts of God; (b) flood, tsunami, fire, earthquake, explosion; (c) epidemics, pandemics, including the 2019 novel coronavirus pandemic (COVID-19); (d) war, invasion, hostilities (whether war is declared or not), terrorist threats or acts, riot, or other civil unrest; (e) government order, law or actions; (f) embargoes or blockades in effect on or after the date hereof; (g) national or regional emergency; (h) strikes, lockouts, labor stoppages or slowdowns, labor disputes, or other industrial disturbances; (i) shortage of adequate power or telecommunications or transportation facilities; (j) failure of any governmental or public authority to grant a necessary license or consent; (k) other similar events beyond the reasonable control of the Impacted Party. The Impacted Party shall promptly give notice of the Force Majeure Event to the other party, stating the period of time the occurrence is expected to continue. The Impacted Party shall use commercially reasonable efforts to end the failure or delay and ensure the effects of such Force Majeure Event are minimized. The Impacted Party shall resume the performance of its obligations as soon as reasonably practicable after the removal of the cause. In the event that the Impacted Party’s failure or delay remains uncured for a period of ten (10) consecutive days following written notice given by it under this Section 23, the other party may thereafter terminate this Order upon seven (7) days’ prior written notice.

- Cumulative Remedies

The rights and remedies under this Order are cumulative and are in addition to and not in substitution for any other rights and remedies available at law or in equity or otherwise.

- Notices

All notices, request, consents, claims, demands, waivers and other communications hereunder (each, a “Notice”) shall be in writing and addressed to the parties at the addresses set forth on the Purchase Order or to such other address that may be designated by the receiving party in writing. Notices sent in accordance with this Section will be deemed effectively given: (a) when received, if delivered by hand, with signed confirmation of receipt; (b) when received, if sent by a nationally recognized overnight courier, signature required; (c) when sent, if by facsimile or email (in each case, with confirmation of transmission) if sent during the addressee’s normal business hours, and on the next business day if sent after the addressee’s normal business hours.

- Severability

If any provision of this Order or application thereof is found invalid, illegal or unenforceable by law, the remainder of this Order will remain valid, enforceable and in full force and effect, and the parties will negotiate in good faith to substitute a provision of like intent and effect.

- Survival

Provisions of this Order which by their nature should apply beyond their terms will remain in force after any termination or expiration of this Order including, but not limited to, the following provisions: Section 8 (Warranties), Section 11 (Set-off), Section 16 (Insurance), Section 17 (Compliance with Laws), Section 18 (Governing Law and Disputes), Section 21 (Indemnification), Section 23 (Confidential Information), and this Section 28 (Survival).

ANNEX A

- Consignee details and required shipping documents

| Country | Delivery address | Consignee details | Shipping documents |
| --- | --- | --- | --- |
| Mainland Tanzania | Morogoro Regional Referral Hospital - Morogoro, Mbeya Regional Referral Hospital - Mbeya, Songea Regional Referral Hospital - Ruvuma, Dodoma Regional Referral Hospital – Dodoma and Manyara Regional Referral Hospital - Manyara | " PERMANENT SECRETARY, MINISTRY OF HEALTH TANZANIA, P. O. BOX 743 DODOMA, TANZANIA Tel: 255-26-2323267/5 E-mail: ps@afya.go.tz " | "-Airway Bill (on consignee address), '-Packing List, ‘MSDS if/where applicable, '-Quality control (CE/FDA/etc.) and or Inspection documents for the goods, '-Certificate of Origin, '-Invoice (on consignee address)" |

ANNEX B

- Supply and installation requirements

| Category | Requirement |
| --- | --- |
| Design | According to HTM-02-01 or NFPA99 |
|  | BOQ aligns with DWGs |
|  | Claims of all flows to Tus |
|  | Claims of maximum pressure loss through system |
|  | Documentation of personnel training/qualifications, which may include: - CV of lead system design engineer - Certifications of personnel installing the system - Summary of training program supplier requires of technical team involved in design & install |
| Training | Certifications of personnel and CV of the Lead System Design Engineer |
|  | Documentation summarizing the training program that the supplier requires of all engineers involved in medical gas system installation and design |
| Warranty | All components should have at least 2 years’ warranty period after commissioning |
|  | The supplier must ensure the availability of spare parts for at least 5 years |
|  | Within the warranty period, the manufacturer will be responsible for the prompt repair of malfunctioning equipment within the system |
| Testing and commissioning | On-site: Inspection, testing and commission should be done before handover |
| Regulatory and Standards for pipelines | Certificate of Quality Management System (either ISO 9001 or ISO 13485 with scope clearly defined) |
|  | ISO 7396-1: Medical gas pipeline systems — Part 1: Pipeline systems for compressed medical gases and vacuum Note: Statement of compliance to be provided by the company carrying out design and installation |
|  | ISO 9170-1: Terminal units for medical gas pipeline systems |
|  | BS EN 13348: Copper and coppery alloys. Seamless, round copper tubes for medical gases or vacuum |
|  | BS EN 1057: Copper and copper alloys. Seamless, round copper tubes for water and gas in sanitary and heating applications (*n.b. this standard is used for dimensioning of piping) |
|  | EN 1254-1: Copper and copper alloys - Plumbing fittings - Fittings with ends for capillary soldering or capillary brazing to copper tubes |
|  | EN 1254-4: Copper and copper alloys - Plumbing fittings - Fittings combining other end connections with capillary or compression ends |
| Regulatory and Standards for medical devices | Certified Quality Management Systems (ISO 13485) |
|  | Regulatory approval under SRA (CE under MDR or US FDA) for all medical devices included in the BOQ such as manifolds, terminal units, flowmeters, and humidifiers |
|  | ISO 10524-2: Pressure regulators for use with medical grade gases (for manifolds) |
|  | ISO 21969: High-pressure flexible connections for use with medical gas systems (for manifolds) |

- Specifications of automatic oxygen change over panel and pipeline system

| S.NO | ITEM DESCRIPTION |
| --- | --- |
| 1.2 | Automatic oxygen change over panel |
|  | Supply, installation, testing and commissioning of fully automatic gas changeover facility as per BS EN ISO 7396-1:2007+A2:2010 standard |
|  | The unit is supplied as a complete factory tested package. |
|  | The plant includes exhaust, relief valve, pressure switch, supply isolation valve, on-return valve and all accessories to make the system functional. |
|  | control type- fully automatic |
| 1.3 | MEDICAL OXYGEN GAS TERMINAL UNITS |
|  | Supply, Installation, testing and commissioning of medical gas terminal unit. |
|  | The unit is supplied as a complete package, fully tested prior to shipping. The unit includes maintenance valve safety nut, check valve, flush box with base block seal; O-ring , plug -in coupling, internal and external gas identification, release bushing and cover plate. |
|  | Must fulfill HTM 02 01 requirements. |
|  | oxygen terminals (wall mounted) shall be (BS type), Oxygen terminal unit shall meet ISO 9170-1:2017 Terminal units for medical gas pipeline systems — Part 1 |
| 1.4 | AREA ALARM UNIT |
|  | Supply, Installation, testing and commissioning of medical gas area alarm module. |
|  | The unit is supplied as a complete package, fully tested prior to shipping. shall be used for all medical gases specified on the drawing. |
|  | The module must fulfill HTM 02 01 requirements. |
|  | 1 GASES AREA ALARM UNITS |
| 1.5 | ZONE SERVICE UNITS |
|  | Supply, Installation, testing and commissioning of medical gas Zone service Valve unit with valves, pressure gauges and NIST connect fully comply to BS ES ISO 7396-1:2007+A2 2010 |
|  | The unit is supplied as a complete package, fully tested prior to shipping. The unit equipped with stamped gas identification shut-off valve (100% leakage free) The unit shall be used for all medical gases specified on the drawing. |
|  | Note service valve unit can also be integrated with area alarm in one control panel as per HTM 01 02 |
|  | The module must fulfill HTM 02 01 requirements. |
|  | 1 GASES AREA valve box |
| 1.6 | OXYGEN FLOW METER W/HUMIDIFIER (Adult) |
|  | Supply of medical oxygen gas flow meter with humidifier compatible with BS type wall terminal units |
|  | As per specification in the attachment, including regulatory & standards: bears CE marking under MDR, lS0 13485 |
|  | 0-15 L/min,accuracy 10%, dual taper graduations 0.5 L/min (0–5 L/min range) and 1 L/min (5 L/min – maximum range) |
|  | The module must fulfill HTM 2022 requirements. |
|  | FLOW METER with Humidifier |
|  | OXYGEN FLOW METER W/HUMIDIFIER (Pediatrics) |
|  | Supply of medical oxygen gas flow meter with humidifier compatible with BS type wall terminal units |
|  | As per specification in the attachment, including regulatory & standards: bears CE marking under MDR, lS0 13485 |
|  | 0-5 L/min, accuracy 10%, dual taper graduations 0.5 L/min (0–5 L/min range) |
|  | The module must fulfill HTM 2022 requirements. |
|  | FLOW METER with Humidifier |
|  | OXYGEN FLOW METER W/HUMIDIFIER (Neonate) |
|  | Supply of medical oxygen gas flow meter with humidifier compatible with BS type wall terminal units |
|  | As per specification in the attachment, including regulatory & standards: bears CE marking under MDR, lS0 13485 |
|  | 0-3.5L/min, accuracy 10%, dual taper graduations 0.5 L/min (0–3.5 L/min range) |
|  | The module must fulfill HTM 2022 requirements. |
|  | FLOW METER with Humidifier |
| 1.7 | Medical copper pipe |
|  | Supply, installation, testing and commissioning of copper pipes for medical gases including fittings, valves, expansion, bellows, hangers, brackets, supports and all accessories, as per BS EN 13348:2008 Standard |
|  | should conform to ASTM B-280/B-819 specifications, is specially cleaned, de-burred, purged and pressurized with nitrogen gas, and features easy to remove, installer friendly, rubber plugs. |
|  | requires the use of Type K or L copper tube (see ASTM B 819). |
|  | Dia. 12mm |
|  | Dia. 15mm |
|  | Dia. 22mm |
|  | Dia. 28mm |
|  | Dia. 32 mm |
| 1.8 | Line Valves Size of the valves |
|  | Size of the valves |
|  | 1/2" Ball Valve Set, with Coupling to copper pipe - 15mm |
|  | 3/4" Ball Valve Set, with Coupling to copper pipe - 22mm |
|  | 1" Ball Valve Set, with Coupling to copper pipe - 28mm |
|  | 1" Ball Valve Set, with Coupling to copper pipe - 35mm |
| 1.9 | Support structure |
|  | Supply and install all the necessary support structure for the medical gas system pile line and Equipment's as per the drawing and HTM standard. |
| 1.10 | Copper fittings and accessories |
|  | Supply and install all the necessary accessories and fittings for proper installation of the medical pipeline in accordance to HTM standard please check the attached fitting and accessories for reference but not limited to. |
|  | copper fitting from size 9mm to 35mm Elbow, Tee, Tee-reducer, socket, reducer |
|  | Elbow Size (mm) outside diameter |
|  | 12 |
|  | 15 |
|  | 22 |
|  | 28 |
|  | 35 |
|  | Tee Size (mm) outside diameter |
|  | 12 |
|  | 15 |
|  | 22 |
|  | 28 |
|  | 35 |
|  | Tee with reducer Size (mm) outside diameter |
|  | 15x12x15 |
|  | 22x15x22 |
|  | 22x12x22 |
|  | 28x22x28 |
|  | 35x28x35 |
|  | Reducer Size (mm) outside diameter |
|  | 12x9 |
|  | 15x12 |
|  | 22x15 |
|  | 28x22 |
|  | 35x28x35 |
|  | Socket Size (mm) outside diameter |
|  | 12 |
|  | 15 |
| 1.11 | Pipe trunking |
|  | Supply and install all the necessary Trunking for the medical gas system pile line and Equipment's as per the drawing and HTM standard. width 100mmx50mm |
| 1.11 | Copper pipe Insulation Supply and install Flexible Closed Cell Elastomeric Pipe Insulation. 20mm insulation , vapor barrier with aluminum foil cladding. insulation should be as per ASTM C 518. |

- Flowmeter specification

| S.NO | ITEM DESCRIPTION |
| --- | --- |
| 1 | Oxygen Flowmeter |
| 1.1 | Specification |
|  | Oxygen Flowmeter Device suitable for use with medical purpose in the health facility |
|  | Thorpe tube flowmeter type, contains inlet and outlet port, a flow regulator, a valve and a clear measuring tube |
|  | Flowmeters to measure and regulate flow from an already pressure-reduced and regulated oxygen source to the patient or other medical device |
|  | Pressure compensated flowmeters, calibrated at 345–380 kPa (3.4–3.8 bar, 50–55 psi) inlet gauge pressure. |
|  | Max gauge inlet pressure 690 kPa (6.9 bar, 100 psi). |
|  | Flow adjustment knobs to have rough surface to prevent slipping. |
|  | Flowmeters calibrated to the following flow range, |
|  | 0-15 L/min, accuracy 10%, dual taper graduations 0.5 L/min (0–5 L/min range) and 1 L/min (5 L/min – maximum range) for adults |
|  | 0-5 L/min, accuracy 10%, dual taper graduations 0.5 L/min for Pediatrics |
|  | 0-3.5 L/min, accuracy 10%, dual taper graduations 0.5 L/min for Neonatology, |
|  | All minimum flowrates to be zero when fully closed |
|  | All graduations to be clearly visible for 270 degrees (most breadth for provider vantage points) |
|  | Inlet and outlet ports to be clearly specified and will in part be determined by use case (suitable for connection to centralized system, cylinders, concentrators, or compressors): |
|  | Piped source inlet: Connection to a terminal unit / bedside unit from a piped oxygen network to be BS (3/8-inch BSP female, “British Standard”) |
|  | Outlets: DISS (9/16 inch-18) male with “Christmas tree” barbed tubing adaptor |
|  | Flowmeter material: |
|  | Column to be transparent, clear, shatter-resistant, medical-grade polymer (polypropylene, polycarbonate) |
|  | Hardware/valves: Brass/steel/aluminum |
|  | All materials in contact with oxygen certified for medical use. |
|  | Internal parts (e.g. valve, inlet filter if present), replaceable by user. |
|  | Environmental: |
|  | Capable of being stored in ambient temperature of at least 5–50 °C, relative humidity of at least 15–95% non-condensing. |
|  | Suitable for continuous operation in ambient temperature of at least 5–45 °C, relative humidity of at least 15–90% non-condensing. |
|  | Specific requirements for altitude may be required, depending on the installation site. |
|  | Disinfect able with hospital grade detergents. |
| 1.2 | Warranty: 2 years, since it is almost maintenance free devices |
| 1.3 | QMS : |
|  | ISO 13485 (medical device QMS) |
|  | ISO 14971 (application of risk management) |
|  | ISO 15002: Flow-metering devices for connection to terminal units of medical gas pipeline systems |
| 1.4 | Regulatory: |
|  | CE Marks conforming to Medical Device Directive 93/42/EEC or FDA |
|  | ISO 32 color coding of oxygen for medical use — Marking for identification of content white color and shows or indicate O2 As a type of medical gas |
|  | ISO 5359 Low-pressure hose assemblies for use with medical gases. |
|  | ISO 15001 Anesthetic and respiratory equipment – Compatibility with oxygen. |
|  | ISO 15002 Flow-metering devices for connection to terminal units of medical gas pipeline systems. |
|  | ISO 15223-1 Medical devices – Symbols to be used with medical device labels, labelling and information to be supplied – Part 1: General requirements. |
|  | ISO 18082 Anesthetic and respiratory equipment – Dimensions of non-interchangeable screw-threaded (NIST) low-pressure connectors for medical gases. |
|  | ISO 18562 Biocompatibility evaluation of breathing gas pathways in healthcare applications. |
| 1.5 | Packaging: |
|  | Name and/or trademark and address of the manufacturer. |
|  | Product name. |
|  | Product reference. |
|  | Type of product and main characteristics. |
|  | Performance testing information against the mentioned standards. |
|  | Lot number prefixed by the word “LOT” (or equivalent harmonized symbol). |
|  | Information for particular storage conditions (temperature, pressure, light, humidity, etc.), as appropriate (or equivalent harmonized symbol), if applicable. |
|  | Information for handling, if applicable (or equivalent harmonized symbol). |
|  | If the packaging is not transparent, it must bear a diagram (preferably actual size) showing the essential parts of the product and indicating the position of the product in the packaging. |
|  | Gross Weight. |
|  | Cubic Measurement. |
|  | All indicated at least in English. |

- Humidifier Specification

| S.NO | DESCRIPTION |
| --- | --- |
| 1 | Humidifier: Reusable humidifier for oxygen therapy and ventilation system in the health facility setup |
| 1.1 | Technical specification |
|  | Reusable humidifier for oxygen therapy and ventilation/anesthesia inspiratory lines. |
|  | Non-heated humidifier - ambient temperature functionality. |
|  | Bubble-through humidification system. |
|  | Unbreakable or shatter resistant. |
|  | Transparent humidification bottle |
|  | Graduated, graduation shall show minimum and maximum water level. |
|  | Humidification chamber working volume at least 150 mL, not greater than 500 mL. |
|  | Detachable metal or rigid durable polymer cap with gas connectors. |
|  | Pressure relief safety valve, ≥ 14 kPa (0.1 bar, 2 psi) pressure rating. |
|  | DISS connectors for inlet. |
|  | 6 mm barbed connector for outlet. |
|  | Flow rate capacity up to 15 L/min. |
|  | Must be capable of disinfection. |
|  | Materials, all to be certified for medical use: |
|  | Cap and connectors made of brass/steel/other biocompatible metal or polymer |
|  | Bottle and tubes made of polypropylene, polycarbonate or equivalent biocompatible plastic/polymer |
|  | Pressure valve made of brass chromium plated or equivalent metal |
|  | Supplier must define decontamination procedure. |
| 1.2 | Warranty: Min. 2 years |
| 1.3 | Standards: ISO 13485 (medical device QMS) |
| 1.4 | Regulatory: |
|  | CE mark conforming to Medical Device Directive 93/42/EEC or FDA |
| 1.5 | Product performance standards: |
|  | ISO 15001 Anesthetic and respiratory equipment – Compatibility with oxygen. |
|  | ISO 15223-1 Medical devices – Symbols to be used with medical device labels, labelling and information to be supplied – Part 1: General requirements. |
|  | ISO 18562 Biocompatibility evaluation of breathing gas pathways in healthcare applications. |
|  | ISO 18562-1 Biocompatibility evaluation of breathing gas pathways in healthcare applications – Part 1: Evaluation and testing within a risk management process. |
| 1.6 | Packaging: |
|  | Name and/or trademark and address of the manufacturer. |
|  | Product name. |
|  | Product reference. |
|  | Type of product and main characteristics. |
|  | Performance testing information against the mentioned standards. |
|  | Lot number prefixed by the word "LOT" (or equivalent harmonized symbol). |
|  | Expiry date by year and month, prefixed by the word "EXP" (or equivalent harmonized symbol). |
|  | Information for particular storage conditions (temperature, pressure, light, humidity, etc.), as appropriate (or equivalent harmonized symbol), if applicable. |
|  | Information for handling, if applicable (or equivalent harmonized symbol). |
|  | If the packaging is not transparent, it must bear a diagram (preferably actual size) showing the essential parts of the product and indicating the position of the product in the packaging. |
|  | Gross Weight. |
|  | Cubic Measurement. |
|  | All indicated at least in English. |

APPENDIX- 1: DRAWINGS

APPENDIX- 2 – MATRIX ISSUE FOR NEGOTIATION

ITB FOR INSTALLATION, TESTING & COMMISSIONING OF MEDICAL OXYGEN VIE TANKS, CONTROL PANEL & VAPORIZER AT VARIOUS HEALTH FACILITIES IN MAINLAND TANZANIA

MATRIX OF ISSUES NEGOTIATED

PROSPECTIVE SUPPLIER/CONTRACTOR (BIDDER): ____________________

BID ID NUMBER: CHAI-TZ-EAPOA-002/25

CLIENT: CLINTON HEALTH ACCESS INITIATIVES (CHAI)

DATE: _____ SEPTEMBER 2026

| SIGNATURE: ___________________________________ |  | SIGNATURE: __________________________ |
| --- | --- | --- |
| NAME: Dr. Esther Mtumbuka |  | NAME: ___________________ |
| FOR: CLINTON HEALTH ACCESS INITIATIVES |  | FOR: VENDOR |
| DATE: ________________________________ 2026 |  | DATE: _____________________ 2026 |